# 05_Process: Process Automation

Your reference places `05_Process → Process automation` immediately after Discrete Automation and before Batch Automation. Pasted markdown(1)

The reference gives the topic name but does not provide a detailed definition, so the detailed technical explanation below is the foundational content for studying this topic. The next topic, Batch Automation, is kept separate.

# 1. What is Process Automation?

Process automation is the use of automatic control systems to monitor, control, and regulate a physical process, particularly processes involving continuously or semi-continuously varying physical quantities.

The important idea is not individual parts.

Instead, the system is concerned with process variables such as:

Temperature

Pressure

Flow

Level

Speed

pH

Density

Composition

Humidity

Concentration

The automation system continuously measures these variables and adjusts the process to achieve the desired operating condition.

A simplified model is:

Process

↓

Measurement

↓

Controller

↓

Control action

↓

Process

↑

Feedback

This is the fundamental idea behind process automation.

# 2. The Core Difference from Discrete Automation

You just studied:

Discrete Automation

The main question is often:

What operation should happen next?

Process automation is more concerned with:

What value should the process variable be maintained at?

For example:

### Discrete

Part detected?

↓ YES

Clamp

↓

Machine

↓

Unclamp

### Process

Temperature = 85°C

↓

Compare with setpoint

↓

Temperature too low?

↓

Increase heating

↓

Temperature rises

↓

Approaches 85°C

↓

Reduce heating

So the emphasis changes from sequence to regulation/control of process variables.

# 3. The Basic Process-Control Loop

The most important diagram in this topic is:

SETPOINT

│

↓

┌─────────────┐

│             │

│ Controller  │

│             │

└──────┬──────┘

│

↓

Output

│

↓

Actuator

│

↓

PROCESS

│

↓

Sensor

│

↓

Measurement

│

└──────────→ Controller

This is a closed-loop control system.

The controller continuously receives information about the actual process condition and adjusts the output.

# 4. Setpoint

The setpoint, usually abbreviated SP, is the desired value of a process variable.

Example:

Temperature SP = 80°C

The controller's job is to maintain the actual temperature near 80°C.

Other examples:

Pressure SP = 5 bar

Flow SP = 100 L/min

Level SP = 70%

Speed SP = 1500 RPM

# 5. Process Variable

The process variable, or PV, is the actual measured value.

Example:

SP = 80°C

PV = 74°C

The controller sees that the actual temperature is below the desired temperature.

Therefore, it may increase the heating output.

Another example:

SP = 80°C

PV = 84°C

Now the actual temperature is above the desired value.

The controller may reduce heating or increase cooling.

# 6. Error

The controller generally considers the difference between the desired and actual values.

A simplified representation is:

Error = Setpoint - Process Variable

Example:

SP = 80°C

PV = 74°C

Error = 80 - 74

= +6°C

The controller uses this error to determine an appropriate control action.

This concept is fundamental to closed-loop control.

# 7. Manipulated Variable

The manipulated variable, often called MV, is the variable the controller changes to influence the process.

For example:

### Temperature control

PV = Temperature

MV = Heater output

### Flow control

PV = Flow rate

MV = Control valve position

### Pressure control

PV = Pressure

MV = Valve position / compressor output

### Level control

PV = Tank level

MV = Inlet or outlet flow

So:

SP

↓

Controller

↓

MV

↓

Process

↓

PV

↓

Feedback

# 8. Sensor / Transmitter

The process variable has to be measured.

Typical measurement devices include:

### Temperature

RTD

Thermocouple

Temperature transmitter

### Pressure

Pressure transmitter

Pressure switch

### Flow

Magnetic flowmeter

Coriolis flowmeter

Vortex flowmeter

Differential-pressure flow measurement

### Level

Ultrasonic level transmitter

Radar level transmitter

Differential-pressure level measurement

Float-based measurement

### Composition

pH analyzer

conductivity analyzer

gas analyzer

concentration analyzer

The measurement device converts a physical condition into a usable signal.

# 9. Transmitter

A transmitter is commonly used to convert a measured physical quantity into a standardized industrial signal.

For example:

Temperature

↓

Temperature transmitter

↓

4–20 mA

↓

Controller

Similarly:

Pressure

↓

Pressure transmitter

↓

4–20 mA

↓

Controller

This is why 4–20 mA is so important in traditional industrial process automation.

# 10. Why 4–20 mA?

A common analog instrumentation signal is:

4–20 mA

For example:

4 mA  →  0 bar

12 mA →  5 bar

20 mA → 10 bar

The controller can determine the process value from the current.

An important advantage is that 4 mA represents the lower end rather than 0 mA.

Therefore:

0 mA

can potentially indicate:

broken wire

loss of power

transmitter failure

disconnected circuit

while:

4 mA

can represent a legitimate measured zero.

This is called live zero.

# 11. Controller

The controller receives the measurement and determines the required control action.

Controllers may include:

PLC

dedicated PID controller

DCS controller

industrial PC

process controller

The exact architecture depends on the application.

In many modern plants, PLCs are absolutely capable of process control.

Therefore:

Process automation does not automatically mean DCS.

DCS is strongly associated with process industries, but PLC-based process control is also common.

# 12. PID Control

One of the most important concepts in process automation is PID control.

PID means:

P = Proportional

I = Integral

D = Derivative

A PID controller calculates a control output based on the behavior of the error.

Conceptually:

Error

│

├── P

├── I

└── D

↓

Controller output

The purpose is to make the process variable follow the desired setpoint.

# 13. Proportional Control

The proportional component reacts to the current error.

If the error becomes larger, the controller generally produces a larger corrective action.

Example:

SP = 100°C

PV = 80°C

Error = 20°C

→ larger correction

PV = 95°C

Error = 5°C

→ smaller correction

Conceptually:

P responds to how far away the process currently is from the setpoint.

# 14. Integral Control

The integral component responds to the accumulated error over time.

This is important when a system has a persistent offset.

Example:

SP = 100°C

PV remains around 97°C

There is a persistent 3°C error.

The integral action accumulates that error and increases the control effort until the steady-state error is reduced.

Conceptually:

I responds to how long and how much error has accumulated.

# 15. Derivative Control

The derivative component responds to the rate of change of error.

It attempts to anticipate where the process is heading.

For example, if temperature is rising very rapidly toward the setpoint, derivative action can help reduce excessive overshoot.

Conceptually:

D responds to how quickly the error is changing.

# 16. PID Mental Model

A useful memory aid:

P = Present error

I = Past accumulated error

D = Future tendency / rate of change

More precisely:

P → current error

I → accumulated error

D → rate of change of error

This is one of the most useful interview-level concepts in process automation.

# 17. Example: Temperature Control

Consider an industrial oven.

Required temperature:

SP = 200°C

Actual temperature:

PV = 180°C

The controller detects:

Error = +20°C

It increases heater output.

Then:

PV = 190°C

The error decreases.

Then:

PV = 198°C

The controller reduces the heating demand.

Eventually:

SP ≈ PV

200°C ≈ 200°C

The controller continuously adjusts the output to maintain the desired temperature.

# 18. Open-Loop vs Closed-Loop

This distinction is important.

## Open-loop control

The controller does not use feedback from the process to correct the output.

Example:

Turn heater ON for 10 minutes

The system does not care whether the actual temperature reaches 100°C.

Timer

↓

Heater

↓

Process

## Closed-loop control

The system measures the actual process condition.

Setpoint

↓

Controller

↓

Heater

↓

Process

↓

Temperature sensor

↓

Controller

Now the system can continuously correct the process.

Most important process control applications use closed-loop control.

# 19. Feedback

Feedback is the information returned from the process to the controller.

Example:

Setpoint = 100°C

Controller

↓

Heater

↓

Oven

↓

Temperature

↓

RTD

↓

Temperature transmitter

↓

PLC/PID

The controller knows what actually happened because of feedback.

Without measurement, meaningful closed-loop regulation is impossible.

# 20. Common Process Variables

The major process variables are worth memorizing.

### Temperature

°C

°F

K

### Pressure

bar

kPa

MPa

psi

### Flow

L/min

m³/h

kg/h

### Level

%

mm

m

### Speed

RPM

### pH

pH

### Composition

Examples:

%

ppm

The exact variable and units depend on the process.

# 21. Common Process Industries

Process automation is especially important in industries involving continuous or large-scale process variables.

Examples:

oil and gas

petroleum refining

chemical plants

pharmaceutical manufacturing

food and beverage

power generation

water treatment

wastewater treatment

cement

steel

paper

glass

utilities

thermal processing

But process automation is not restricted to these industries.

A discrete manufacturing facility can also contain process-control systems.

For example:

furnace temperature

paint booth temperature

coolant pressure

compressed-air pressure

water treatment

lubrication systems

HVAC

chemical dosing

So a factory can contain both discrete and process automation.

# 22. A Manufacturing Plant Can Use Both

This is extremely important for your industrial background.

Imagine an automotive plant.

The production line may be:

Robot

↓

Welding

↓

Assembly

↓

Inspection

This is largely discrete automation.

But the same plant may have:

Compressed air pressure

Water flow

Paint temperature

Oven temperature

Boiler pressure

Cooling-water temperature

HVAC

These are process-control applications.

Therefore:

Discrete automation and process automation are not mutually exclusive within the same plant.

A modern factory can contain both.

# 23. Example: Paint Shop

A paint shop is a good example because it can combine both types.

### Discrete side

Body detected

↓

Robot starts

↓

Paint operation

↓

Robot complete

↓

Body transferred

### Process side

Paint temperature

Paint flow

Booth pressure

Airflow

Oven temperature

Humidity

The robots and material handling are predominantly discrete.

The temperature, pressure, flow and environmental control are process-oriented.

One manufacturing system can therefore contain both control philosophies.

# 24. Process Automation Architecture

A simplified architecture:

SUPERVISORY / HMI / SCADA

│

↓

PLC / DCS / PID

│

┌─────────────┼─────────────┐

↓             ↓             ↓

Transmitter     Controller     Actuator

│                           │

↓                           ↓

PROCESS ←───────────────────────

│

↓

Measurement

│

└────────→ Controller

For a more detailed instrumentation chain:

Physical variable

↓

Sensor

↓

Transmitter

↓

Signal

↓

I/O

↓

Controller

↓

Control output

↓

Final control element

↓

Process

# 25. Final Control Element

The controller itself generally does not directly manipulate the physical process.

It sends a command to a final control element.

Examples:

control valve

damper

heater

pump

motor

VFD

compressor

actuator

Example:

Temperature controller

↓

4–20 mA output

↓

SCR / power controller

↓

Heater

↓

Oven temperature

Or:

Flow controller

↓

Valve command

↓

Control valve

↓

Flow changes

# 26. Control Valve

Control valves are extremely common in process automation.

A simplified system:

Flow transmitter

↓

Flow controller

↓

Valve command

↓

Control valve

↓

Process flow

↓

Flow transmitter

Suppose:

SP = 100 L/min

PV = 80 L/min

The controller may increase valve opening.

If:

PV = 105 L/min

the controller may reduce the valve opening.

This continuous correction is characteristic of process control.

# 27. Pump and VFD Control

A process variable can also be controlled by changing motor speed.

Example:

Pressure transmitter

↓

Pressure controller

↓

VFD speed command

↓

Pump

↓

Process pressure

↓

Pressure transmitter

If pressure is too low:

Increase pump speed

If pressure is too high:

Reduce pump speed

This is process automation combined with variable-speed motor control.

# 28. Process Automation and DCS

A Distributed Control System, or DCS, is strongly associated with process automation.

A DCS typically provides:

distributed controllers

process I/O

operator stations

engineering stations

alarms

trends

historian integration

control loops

supervisory functions

communication

A simplified structure:

Operator Station

↓

DCS Network

↓

Controllers

↓

I/O

↓

Transmitters / Valves

↓

Process

However:

Process automation ≠ DCS only.

PLC-based systems, dedicated controllers and other architectures are also used.

# 29. PLC vs DCS in Process Automation

A simplified comparison:

| PLC | DCS |
| --- | --- |
| Strong in machine/sequence control | Strong in large process control |
| Fast discrete logic | Large numbers of control loops |
| Common in discrete automation | Common in process industries |
| Machine/cell/line applications | Plant/process applications |
| Modular architecture | Distributed architecture |
| Can perform PID/process control | Designed strongly around process control |

But modern systems overlap heavily.

A PLC can perform sophisticated PID control.

A DCS can handle discrete logic.

Therefore, avoid treating the boundary as absolute.

# 30. Alarms

Process automation relies heavily on alarms.

Examples:

High Temperature

Low Temperature

High Pressure

Low Pressure

High Level

Low Level

High Flow

Low Flow

Transmitter Failure

Communication Failure

Controller Failure

An alarm informs the operator that the process has entered an undesirable or abnormal condition.

A key distinction:

An alarm informs. A control action regulates. A trip protects by taking the process to a safer state.

Your study index has separate topics for Alarm, Fault and Trip, so those should be treated in greater detail later rather than collapsing them here.

# 31. Process Trips

A trip is generally associated with automatically taking equipment/process action when a dangerous or unacceptable condition occurs.

Example:

High pressure

↓

Trip condition

↓

Pump shutdown

or:

Very high temperature

↓

Safety action

↓

Heater shutdown

The exact behavior depends on the process and safety design.

This is different from simply displaying an alarm.

# 32. Process Automation and Safety

Process plants can contain hazardous conditions involving:

high pressure

high temperature

combustible materials

toxic chemicals

flammable gases

high energy

rotating machinery

Therefore process automation can interact closely with:

safety instrumented systems

emergency shutdown systems

interlocks

trips

pressure protection

fire and gas systems

But process control and process safety should not be treated as the same thing.

The basic control system regulates the process.

Safety systems are designed to protect people, equipment and the environment when hazardous conditions occur.

# 33. Cascade Control

A more advanced process-control structure is cascade control.

Instead of one controller directly controlling the final element:

Main controller

↓

Valve

↓

Process

you can have:

Primary controller

↓

Secondary controller

↓

Valve

↓

Process

For example, temperature control may manipulate a secondary flow loop.

Conceptually:

Temperature SP

↓

Temperature Controller

↓

Steam Flow SP

↓

Flow Controller

↓

Steam Valve

↓

Heater

↓

Temperature

This allows the system to respond more effectively to disturbances.

For your current Fundamentals topic, understand the concept. Detailed cascade tuning belongs to more advanced control study.

# 34. Feedforward Control

Another advanced concept is feedforward control.

Instead of waiting for the process variable to change, the controller responds to a measured disturbance.

Example:

Disturbance detected

↓

Feedforward calculation

↓

Control action

↓

Process

This can be combined with feedback control.

Conceptually:

Disturbance

↓

Feedforward ──────┐

↓

Process ←──── Controller

↓

Feedback ────────┘

The important idea:

Feedback reacts after observing the result.

Feedforward attempts to compensate for a disturbance before its full effect appears.

# 35. Process Dynamics

A process does not necessarily respond instantly to an input.

For example:

Heater output increases

↓

Heat transfer occurs

↓

Material temperature slowly increases

↓

Temperature reaches new condition

There may be:

delay

lag

inertia

dead time

time constant

Therefore process automation must account for process behavior over time.

This is one major reason process control differs from simple ON/OFF sequence control.

# 36. ON/OFF Control vs Continuous Control

Not every process controller must use PID.

A simple temperature controller could operate:

Temperature < 90°C

→ Heater ON

Temperature > 100°C

→ Heater OFF

This is ON/OFF control.

It is simple but can produce cycling around the desired range.

A more precise system may use proportional/PID control:

Temperature slightly low

→ Small heating output

Temperature significantly low

→ Large heating output

This gives finer control.

# 37. Analog vs Digital Control

Process automation traditionally makes extensive use of analog measurements.

For example:

Temperature = 173.6°C

Pressure = 5.72 bar

Flow = 84.3 L/min

The controller needs more information than simply:

ON

OFF

But modern digital systems process these analog measurements numerically.

So:

Physical variable → analog/digital measurement → digital controller → analog/digital output → physical process

# 38. Example: Tank Level Control

Consider a water tank.

Desired level:

SP = 70%

Measured level:

PV = 60%

The controller determines that level is too low.

It may increase the inlet valve opening.

Level sensor

↓

Level transmitter

↓

PLC/PID controller

↓

Valve command

↓

Inlet valve opens

↓

Tank level rises

↓

Level transmitter

Eventually:

PV ≈ SP

70% ≈ 70%

The controller reduces the corrective action.

# 39. Example: Pressure Control

Suppose a compressed-air system requires:

SP = 7 bar

Actual:

PV = 6.5 bar

The controller may increase compressor output.

As pressure approaches 7 bar:

PV = 6.9 bar

The controller reduces the required output.

This is closed-loop process control.

# 40. Example: Flow Control

Suppose:

SP = 500 L/min

PV = 450 L/min

The flow controller may increase the control valve opening.

As flow approaches:

500 L/min

the control action is adjusted.

The same control philosophy applies to many process variables.

# 41. Process Automation Troubleshooting

For maintenance, the following chain is extremely useful:

Process variable wrong

↓

Is the process actually wrong?

↓

Is the sensor measuring correctly?

↓

Is the transmitter healthy?

↓

Is the signal reaching the controller?

↓

Is the scaling correct?

↓

Is the controller receiving correct PV?

↓

Is the setpoint correct?

↓

Is the controller output correct?

↓

Is the final control element responding?

↓

Is the process responding?

This prevents the classic maintenance mistake of replacing the transmitter because the HMI value looks wrong, only to discover that someone entered incorrect scaling three years ago and humanity collectively decided it was tomorrow's problem.

# 42. Example of a Signal Chain Fault

Suppose an HMI shows:

Temperature = 250°C

but the actual temperature is approximately:

150°C

Possible fault locations include:

Temperature

↓

Sensor

↓

Transmitter

↓

Wiring

↓

I/O module

↓

PLC scaling

↓

Controller

↓

HMI

The displayed value is the end of a chain.

Therefore:

A wrong displayed process value does not automatically mean the physical process is wrong.

You troubleshoot the measurement chain systematically.

# 43. Process Automation and SCADA

Process automation often integrates with SCADA.

SCADA can provide:

process visualization

trends

alarms

historical data

operator controls

equipment status

reports

Example:

Field Instruments

↓

PLC / DCS

↓

SCADA

↓

Operator

This is where your earlier study of automation architecture connects naturally to process automation.

# 44. Process Data

Process automation generates valuable continuous data.

For example:

Timestamp       Temperature   Pressure   Flow

10:00:01        180.2°C       4.8 bar    420 L/min

10:00:02        180.5°C       4.8 bar    421 L/min

10:00:03        180.8°C       4.9 bar    420 L/min

...

Unlike simple production counts, process data can be sampled continuously.

This is extremely important for:

trends

process optimization

fault detection

predictive maintenance

quality analysis

energy monitoring

historical analysis

This becomes highly relevant later to Industry 4.0.

# 45. Process Automation and Industry 4.0

Process automation provides a large amount of time-series information.

A modern architecture may look like:

Field Instruments

↓

PLC / DCS

↓

SCADA

↓

Historian / Database

↓

Analytics

↓

Dashboard

↓

Decision

Later, this can expand into:

Sensors

↓

PLC / DCS

↓

Edge / Gateway

↓

SQL / Historian

↓

Cloud / Analytics

↓

AI / ML

↓

Optimization

That is where traditional process automation starts connecting with Industry 4.0.

# 46. Discrete vs Process Automation

This comparison is worth memorizing.

| Characteristic | Discrete Automation | Process Automation |
| --- | --- | --- |
| Main object | Individual product/unit | Material/process |
| Main focus | Sequence and operation | Process-variable regulation |
| Typical variables | Part present, position, state | Temperature, pressure, flow, level |
| Typical control | Sequence logic | Feedback/control loops |
| Common controller | PLC/CNC/Robot | PLC/PID/DCS |
| Typical output | Motor, valve, robot, actuator | Valve, pump, heater, VFD |
| Product behavior | Distinct units | Continuous/semi-continuous material |
| Typical example | Assembly line | Chemical process |
| Feedback | Often state/position confirmation | Continuous process measurement |
| Data | Events, states, counts | Time-series process values |

But remember:

The two can coexist in the same machine, line, shop, or plant.

# 47. Discrete + Process in One Machine

Even a single machine can contain both.

Consider a heat-treatment machine:

### Discrete portion

Load part

↓

Close door

↓

Lock door

↓

Start cycle

↓

Complete cycle

↓

Open door

↓

Unload part

### Process portion

Temperature control

Pressure control

Gas flow control

Heating control

Cooling control

So the machine has:

Discrete sequence control

plus

Process control

This is very common in real industrial automation.

# 48. What Makes Process Automation Different?

The strongest conceptual distinction is this:

### Discrete automation

The system is often concerned with:

STATE

EVENT

SEQUENCE

POSITION

PRESENCE

PASS/FAIL

### Process automation

The system is often concerned with:

VALUE

SETPOINT

ERROR

FEEDBACK

TREND

STABILITY

REGULATION

That distinction is much more useful than simply memorizing "PLC vs DCS."

# 49. Important Terms to Know

For this topic, you should be comfortable with these terms:

SP

Setpoint, desired process value.

PV

Process variable, actual measured value.

MV

Manipulated variable, variable adjusted by the controller.

Error

Difference between desired and actual value.

Feedback

Measured process information returned to the controller.

Sensor

Device that detects a physical quantity.

Transmitter

Converts a measured quantity into a standardized signal.

Controller

Determines control action based on the process condition.

Final control element

Device that physically changes the process.

PID

Proportional-Integral-Derivative control.

Loop

A complete measurement-control-actuation path.

Closed loop

Control using feedback.

Open loop

Control without process feedback.

Process variable

Physical quantity being controlled.

# 50. Interview-Level Questions

### Q1. What is process automation?

Process automation is the automatic monitoring and control of physical processes using measurements, controllers and final control elements to maintain desired operating conditions.

### Q2. What are common process variables?

Temperature, pressure, flow, level, speed, pH, composition and humidity.

### Q3. What is the difference between SP and PV?

SP is the desired value.

PV is the actual measured value.

### Q4. What is MV?

The manipulated variable is the quantity adjusted by the controller to influence the process.

### Q5. What is feedback control?

A control method in which the actual process output is measured and returned to the controller so corrective action can be applied.

### Q6. What is PID?

PID stands for Proportional, Integral and Derivative control.

### Q7. What does P do?

Responds primarily to the current error.

### Q8. What does I do?

Responds to accumulated error over time and helps eliminate persistent offset.

### Q9. What does D do?

Responds to the rate of change of error and can help anticipate rapid changes.

### Q10. Is DCS required for process automation?

No. Process automation can use PLCs, PID controllers, DCS and other control architectures.

### Q11. What is a control valve?

A final control element that regulates process flow, pressure, temperature or another process condition by changing fluid flow.

### Q12. What is a 4–20 mA signal?

A common industrial analog instrumentation signal used to represent a measured value or control command.

### Q13. Why is 4 mA used instead of 0 mA as the lower value?

It provides a live zero, allowing 0 mA to potentially indicate a fault such as loss of signal or wiring.

### Q14. Can a manufacturing plant contain both discrete and process automation?

Yes. For example, production machines may use discrete automation while furnaces, paint systems, utilities and HVAC use process automation.

### Q15. Is process automation only for chemical plants?

No. It is used across many industries wherever physical process variables need automatic monitoring and control.

# 51. Final Consolidated Mental Model

Keep this diagram:

PROCESS AUTOMATION

SETPOINT

│

↓

┌─────────────┐

│ CONTROLLER  │

│    PID      │

└──────┬──────┘

│

CONTROL OUTPUT

│

↓

FINAL CONTROL

ELEMENT

│

↓

PROCESS

│

↓

SENSOR

│

↓

TRANSMITTER

│

↓

PROCESS VALUE

│

└─────────────→ CONTROLLER

And the control philosophy:

Measure → Compare → Calculate → Act → Measure Again

Or even more compactly:

SP → Controller → MV → Process → PV → Feedback → Controller

# 52. The Key Difference to Retain

You studied Discrete Automation immediately before this.

Keep the contrast very clear:

DISCRETE

Part / Event / State / Sequence

↓

"What happens next?"

PROCESS

Temperature / Pressure / Flow / Level

↓

"What value should be maintained?"

But in a real industrial system:

MANUFACTURING SYSTEM

│

┌──────────┴──────────┐

↓                     ↓

DISCRETE                 PROCESS

│                     │

PLC / CNC / Robot       PLC / PID / DCS

│                     │

Sequence / State       Regulation / Feedback

│                     │

Parts / Operations     Process Variables

And many real machines contain both.

That is the core of 05_Process → Process automation in your Industry 3.0 Fundamentals sequence. Your reference deliberately puts Batch Automation next, which will introduce another production behavior: producing a defined quantity or batch according to a recipe/process sequence, rather than treating it simply as either discrete or continuous. Pasted markdown(1)