# 04. Scan Time: Watchdog and Cycle-Time Limits

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\02_Scan_Cycle\04_Scan_Time

Scan time determines how quickly a PLC can repeatedly acquire information, execute its control logic, and update its outputs. It affects machine response, sequence timing, diagnostic behavior, and the ability to meet real-time control requirements.

The important distinction is that a PLC can execute its program correctly and still respond too slowly for the application. Correct logic is only one part of a working control system.

## 1. What Is Scan Time?

Scan time is the time taken by a PLC to execute a defined cycle of its control operation. In a traditional cyclic PLC, this generally involves acquiring inputs, executing the program, and updating outputs, along with system overhead.

The precise definition depends on the PLC family and how its tasks are configured. Modern PLCs may use continuous, periodic, event-driven, and other scheduled tasks rather than one universal scan sequence.

A simplified traditional scan cycle is:

+----------------------+

| Input Acquisition    |

+----------+-----------+

|

v

+----------------------+

| Program Execution    |

+----------+-----------+

|

v

+----------------------+

| Output Update        |

+----------+-----------+

|

v

+----------------------+

| System Overhead      |

| Communications       |

| Diagnostics          |

+----------+-----------+

|

v

Next Cycle

This is a conceptual model. Actual input/output updates and communication processing may occur asynchronously or at different intervals.

For example, if a PLC completes a defined cyclic operation in 8 ms, it may repeat that operation approximately 125 times per second.

Cycles per second≈1000Cycle time in ms

For an 8 ms cycle:

10008=125 cycles/s

This calculation describes the cycle rate, not necessarily how frequently every physical input is sampled or every output is updated.

## 2. Important Timing Terminology

Several timing values appear in PLC diagnostics. They are related, but they do not mean the same thing.

| Term | Meaning | Why it matters |
| --- | --- | --- |
| Program execution time | Time spent executing a specific program or task | Identifies computational workload |
| Scan or cycle time | Time associated with a cyclic controller execution cycle | Indicates how frequently cyclic processing repeats |
| Task period | Configured interval between scheduled executions of a periodic task | Determines when the task is intended to run |
| I/O update interval | Interval at which I/O data is transferred or refreshed | Affects how quickly field changes reach the controller |
| Watchdog time | Allowed execution-time limit monitored by the controller or task | Helps detect overruns or abnormal execution |
| Response time | Time between a real-world event and the corresponding system response | Determines actual machine responsiveness |
| Jitter | Variation in execution timing or task start times | Affects timing consistency |
| Minimum scan time | Lowest recorded scan or cycle time | Shows best observed performance |
| Average scan time | Mean recorded scan or cycle time | Shows typical performance |
| Maximum scan time | Highest recorded scan or cycle time during the observation period | Helps reveal worst observed delays |

Example: A PLC might have an average scan time of 6 ms and a maximum of 18 ms. Looking only at the average hides the occasional long cycle that could delay a machine sequence.

Also, a task period of 10 ms does not automatically mean the program takes 10 ms to execute. A task may be scheduled every 10 ms and finish in 2 ms, leaving time before its next scheduled execution.

## 3. What Determines Scan Time?

The controller's workload and scheduling determine how much processing time is required.

| Factor | Effect on execution time |
| --- | --- |
| Program size | More instructions can require more processing |
| Logic complexity | Complex calculations and conditional logic may increase execution time |
| Loops | Large or unbounded loops can consume excessive CPU time |
| Indirect or indexed addressing | May require additional processing compared with simpler access |
| Data handling | Large data copies, array operations, and structure processing add workload |
| Mathematical operations | Complex calculations can increase execution time |
| Communications | Communication processing may consume resources or affect task scheduling |
| Multiple tasks | Competing tasks and task priorities affect execution opportunities |
| Motion and interrupt processing | High-priority or frequent tasks can affect other workloads |
| Diagnostics and monitoring | Online monitoring, trending, and debugging may add overhead, depending on the platform |
| Program organization | Repeated calculations or inefficient routines can waste execution time |
| CPU utilization | Heavy controller workload can affect scheduling and performance |

A large program does not necessarily have a poor scan time. Efficient code on a suitable CPU can execute more quickly than a smaller but inefficient program on a heavily loaded controller.

For maintenance work, compare actual execution measurements rather than judging performance by the number of ladder rungs.

## 4. Why Does Scan Time Vary?

Scan time is not always constant.

Consider a program with several conditional routines:

Main Routine

|

+--> Check Safety Status

|

+--> Check Robot Status

|

+--> IF Fault Detected

|       |

|       +--> Execute Fault Handling

|

+--> IF Production Active

|

+--> Execute Production Sequence

When the machine is idle, some routines may execute less frequently or not execute at all. During production, additional calculations, communication handling, or fault processing may increase the workload.

The result is variation in execution time.

### Jitter

Jitter is the variation in timing from one execution to another.

For example:

| Cycle | Execution time |
| --- | --- |
| 1 | 5 ms |
| 2 | 6 ms |
| 3 | 5 ms |
| 4 | 14 ms |
| 5 | 6 ms |

The 14 ms cycle is an important observation. Even though most cycles are fast, the occasional delay may matter when coordinating with robots, motion systems, or time-sensitive machine operations.

When investigating timing problems, record minimum, average, maximum, and, where available, the distribution of observed times.

## 5. What Is a Watchdog Timer?

A watchdog is a monitoring mechanism that checks whether a controller or task completes its execution within an allowed time.

Its purpose is to detect conditions such as excessive execution time, a stuck execution path, or a task that fails to complete as expected.

For example:

Task Starts

|

v

Program Executes

|

+---- Completes Within Limit ----> Normal Operation

|

+---- Exceeds Allowed Limit -----> Watchdog Fault/Action

The actual response depends on the PLC model, task configuration, and fault-handling settings. Possible outcomes include a task fault, controller fault, transition to a defined fault state, or configured output behavior.

There is no universal watchdog limit for all PLCs. The relevant limit may be a controller default, a configured task watchdog, or another platform-specific timing constraint.

### Watchdog versus process timer

| Watchdog | Process timer |
| --- | --- |
| Monitors execution duration or task completion | Measures time as part of application logic |
| Detects execution overruns or abnormal execution | Controls or monitors a process sequence |
| May trigger a controller or task fault | May set a program bit or trigger an application alarm |
| Related to controller execution integrity | Related to machine behavior |

Example: A clamp is expected to extend within 2 seconds.

A process timer can trigger a clamp-extension timeout alarm if the limit is exceeded.

A watchdog can detect that PLC execution itself exceeded an allowed execution-time limit.

These are entirely different failures. One concerns the machine process; the other concerns controller execution.

A watchdog is also not automatically a safety function. Machine safety must be designed and validated through the appropriate safety architecture and risk assessment.

## 6. Cycle-Time Limits and Task Overruns

Every PLC has practical execution limits determined by its hardware, firmware, task configuration, and application requirements.

For a periodic task, suppose the intended period is 10 ms and the task normally completes in 3 ms.

| Parameter | Value |
| --- | --- |
| Task period | 10 ms |
| Normal execution time | 3 ms |
| Time remaining before next scheduled release | Approximately 7 ms |

Now suppose an unusual condition causes execution to take 12 ms.

The task has exceeded its intended 10 ms period. Depending on the controller and task configuration, this can cause a missed deadline, an overrun indication, delayed execution, or a watchdog fault.

Do not assume every PLC handles overruns identically.

### Why the limit matters

A periodic task may fail to meet its intended schedule.

Time-sensitive calculations may use older-than-expected data.

Other tasks may experience scheduling delays.

Motion or coordinated machine operations may lose timing consistency.

A watchdog may trigger if its applicable limit is exceeded.

A scan time below the watchdog threshold does not prove the application meets its real-time requirements. The machine may require a response within a much shorter deadline than the watchdog permits.

## 7. PLC Scan Time and Machine Response Time

This is one of the most important distinctions in industrial troubleshooting.

Scan time measures controller execution timing. Response time measures the delay from a real-world event to the resulting action.

The complete response path may be:

Sensor Changes State

|

v

Sensor/Input Filtering

|

v

Input Module or Network Update

|

v

Wait for Relevant PLC Task

|

v

Program Executes Logic

|

v

Output Image or Output Command Updates

|

v

Output Module or Network Update

|

v

Actuator Responds

|

v

Feedback Confirms Movement

Every stage can contribute delay.

A conceptual response-time budget is:

aligned T_response ≈ & T_sensor + T_input filter &+T_input update/wait+T_task wait &+T_logic+T_output update &+T_actuator aligned

This is a budgeting model, not a universal exact equation. Some delays overlap, and the timing architecture varies by PLC and I/O system. Avoid double-counting overlapping stages.

### Example: A clamp fixture

A proximity sensor detects that a component is present. The PLC must then command a clamp valve.

Assume, for illustration:

| Stage | Illustrative delay |
| --- | --- |
| Input filtering and acquisition | 2 ms |
| Wait for the next relevant program execution | 8 ms |
| Logic execution | 2 ms |
| Output transfer | 3 ms |
| Valve and actuator response | 45 ms |
| Approximate total | 60 ms |

Even if the PLC logic executes in only 2 ms, the overall response is approximately 60 ms under these assumptions.

The actuator accounts for most of the delay. Optimizing the PLC program alone would have limited effect.

These numbers are illustrative, not specifications for any particular sensor, PLC, or valve.

### Can a PLC miss a short input pulse?

Yes. A physical input pulse may be too short for the configured input filtering, acquisition interval, or controller's input-processing method.

Reducing scan time may help in some configurations, but it does not guarantee detection. Depending on the application, a high-speed input, hardware counter, interrupt/event input, or other appropriate capture mechanism may be required.

## 8. Common Scan-Time and Watchdog Problems

| Symptom | Possible cause | Investigation |
| --- | --- | --- |
| Scan time suddenly increases | New logic, loops, data handling, communications, or increased workload | Compare current and previous diagnostics |
| Watchdog fault occurs | Task exceeds its permitted execution time or fails to complete | Record the fault code and inspect task execution |
| Machine responds intermittently slowly | Scan-time variation, task scheduling, I/O updates, or network delays | Compare maximum timing, jitter, and I/O timing |
| Machine responds slowly despite low scan time | Sensor filtering, remote I/O, task period, output transfer, or actuator delay | Measure the full response path |
| Short sensor pulses are missed | Input filtering or acquisition is too slow for the pulse | Check the input module specifications and capture method |
| Problem appears after a program change | Additional execution load, changed task structure, or new logic path | Compare timing before and after the change |
| Fault occurs only during production | Workload-dependent logic, communications, motion activity, or task contention | Examine timing under representative operating conditions |

## 9. Practical Troubleshooting Procedure

### A. When scan time is high

1.	Read the PLC's current, minimum, maximum, and average scan or task execution measurements, where available.

2.	Check whether the delay affects the entire controller cycle or only a particular task.

3.	Inspect recently changed logic, loops, repeated calculations, and large data operations.

4.	Check task periods, priorities, communications load, and diagnostic activity.

5.	Compare measurements during idle operation and normal production.

6.	Establish a baseline and acceptance limit appropriate to the application.

### B. When a watchdog fault occurs

1.	Record the exact fault code, timestamp, controller state, and affected task.

2.	Check the applicable watchdog configuration and task scheduling.

3.	Review recent program changes and execution paths that may run longer under certain conditions.

4.	Check for unbounded loops, unexpected data conditions, or excessive processing load.

5.	Compare diagnostics with a known-good baseline.

6.	Make changes through the approved change-control process and validate them under controlled conditions.

Do not blindly increase the watchdog limit to make the alarm disappear. That can conceal the underlying problem or allow an application to miss its timing requirements.

### C. When machine response is slow but scan time looks normal

Check the sensor, input filter, I/O update interval, task scheduling, output update, communication path, actuator, and feedback. A controller with a healthy scan time can still sit inside a slow control path.

## 10. How to Optimize Scan Time Safely

Simplify logic while preserving the original behavior.

Eliminate unnecessary repeated calculations and data copying.

Avoid unbounded loops and uncontrolled execution paths.

Use continuous, periodic, or event-driven tasks appropriately for the PLC platform and application.

Review communications and diagnostic workloads when measurements indicate they matter.

Use vendor-provided execution and task diagnostics.

Measure before and after each change.

Define acceptable maximum execution time and response-time requirements.

Validate sequencing, interlocks, fault handling, and safety behavior after changes.

A shorter scan is not automatically a better design. A stable, predictable 8 ms execution cycle may be more useful than a system that usually executes in 3 ms but occasionally takes 25 ms, depending on the application.

## 11. Platform Differences

The concepts are broadly shared across PLC manufacturers, but terminology and scheduling behavior differ.

| Platform family | General point to understand |
| --- | --- |
| Siemens SIMATIC | Execution organization, cyclic processing, interrupts, and process-image arrangements depend on the CPU and configuration |
| Rockwell Automation Logix | Continuous, periodic, and event tasks may be used; task priorities and watchdog configuration matter |
| Mitsubishi MELSEC | Scan processing and interrupt/task behavior depend on the CPU family and program configuration |

Do not assume that a parameter with the same name has identical behavior across manufacturers. When troubleshooting a real machine, use the exact controller model, firmware, task configuration, and relevant manual.

## 12. Interview Questions and Answers

Q1. What is PLC scan time?

The time associated with a PLC's cyclic execution operation. In a traditional cyclic PLC, this generally includes input processing, program execution, and output processing, with platform-specific overhead.

Q2. Why does scan time vary?

Because execution workload, conditional routines, communication activity, task scheduling, interrupts, and diagnostics can change over time.

Q3. What is the function of a watchdog?

It monitors whether controller or task execution completes within an allowed time and can trigger a fault response when the applicable limit is exceeded.

Q4. What is the difference between a watchdog and a timer instruction?

A watchdog monitors execution duration or task completion. A timer instruction measures time for application logic, such as a cylinder timeout or sequence delay.

Q5. Does a low scan time guarantee fast machine response?

No. Input filtering, I/O updates, task scheduling, network delays, output hardware, and actuator response can dominate the total delay.

Q6. Why is maximum scan time important?

It reveals the longest observed execution cycle and can expose occasional delays hidden by the average. It is especially relevant to timing-sensitive applications.

Q7. Can a watchdog fault indicate a program problem?

Yes. Excessive loops, unexpectedly heavy execution paths, or other processing problems can contribute. The exact cause must be confirmed using controller diagnostics.

Q8. Will reducing scan time always solve missed input pulses?

No. The input module's filter and acquisition behavior may be the limiting factor. Hardware capture mechanisms may be necessary.

Q9. Is the watchdog limit the same as the task period?

No. The task period is the intended scheduling interval. The watchdog is an execution-time monitoring limit. Their configuration and relationship depend on the controller.

Q10. Is a PLC watchdog a safety guarantee?

No. It is an execution-monitoring mechanism, not a substitute for a properly designed and validated machine-safety system.

## 13. Practical Study Exercise

For a PLC system you can inspect safely, collect the following information without changing live production settings:

| Item | Information to record |
| --- | --- |
| Controller | Manufacturer, exact model, firmware |
| Execution timing | Current, minimum, average, and maximum scan/task time, where available |
| Task scheduling | Task type, period, priority, execution time |
| Watchdog | Configured limit and relevant fault history |
| Input path | Module type, configured filter, remote I/O update interval |
| Output path | Local or remote output, update interval, actuator type |
| Timing faults | Fault code, timestamp, operating condition |
| Baseline | Normal operation versus the condition in which the problem occurs |

Do not deliberately provoke watchdog faults or test timing limits on a running production machine. Use an approved test environment or controlled maintenance procedure.

## 14. Final Mental Model

Scan time: How long the relevant cyclic controller execution takes.

Task period: How frequently a scheduled task is intended to run.

Watchdog: Whether execution stays within its allowed time limit.

Jitter: How much execution timing varies.

Response time: How long the complete path takes from a physical event to the machine's response.

Cycle-time limit: A timing boundary that the controller or application must respect to operate correctly.

The essential maintenance lesson is this: do not diagnose every slow machine as a slow PLC. Separate controller execution, task scheduling, I/O transfer, communications, and actuator behavior before deciding where the delay originates.

# Next Topic: 03_Diagnostics

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\03_Diagnostics

Topic: Diagnostics: Diagnostic buffer, LEDs, fault codes

This topic will cover how to use controller status LEDs, diagnostic buffers, fault codes, and module/network indicators to identify faults systematically rather than replacing components based on guesswork.