# 03. Diagnostics: Diagnostic Buffer, LEDs, and Fault Codes

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\03_Diagnostics

PLC diagnostics is the process of identifying, interpreting, and isolating faults in a control system using controller status indicators, diagnostic records, error codes, module information, communication status, and program-level fault information.

For industrial maintenance, the goal is not merely to identify that a PLC has a fault. The goal is to determine what failed, where it failed, why it failed, and what evidence confirms the root cause.

A PLC fault can originate from the CPU, power supply, I/O module, field wiring, communication network, program logic, or an external machine condition. Replacing the PLC whenever a machine stops is an expensive way to practice guessing.

## 1. Why PLC Diagnostics Matter

Consider a robot welding station that suddenly stops during production.

Possible causes include:

PLC CPU fault.

Robot communication loss.

Remote I/O module fault.

Sensor or actuator circuit failure.

Safety-system interlock.

Program execution fault.

Network cable or switch failure.

A process condition that has not been satisfied.

The machine symptom may be identical in several cases: the sequence stops. Diagnostics helps distinguish them.

A useful troubleshooting hierarchy is:

Machine Stops

|

v

Check Machine and Controller Status

|

v

Read Diagnostic Buffer and Fault Information

|

v

Identify Affected Device or Function

|

v

Verify Power, Wiring, Network, I/O and Logic

|

v

Confirm Root Cause

|

v

Correct Fault and Validate Recovery

The diagnostic process should follow evidence from the system rather than assumptions based on the visible symptom.

## 2. PLC Diagnostic Architecture

A PLC system provides diagnostic information at several levels.

| Diagnostic level | What it tells you | Example |
| --- | --- | --- |
| CPU/controller | Overall controller condition | CPU fault or operating-mode change |
| Power supply | Power status and supply-related faults | Supply module fault indicator |
| I/O module | Module health and channel status | Input module fault |
| Field device | Sensor or actuator condition | Sensor not detecting a component |
| Communication network | Device connectivity and data exchange | Remote I/O connection timeout |
| Program/application | Logic conditions and execution faults | Invalid data or sequence timeout |
| Safety system | Safety-related status and fault information | Safety interlock not satisfied |

A fault indication identifies a condition, but it does not always identify the root cause.

For example, a remote I/O communication fault may be caused by a damaged cable, failed switch port, loss of module power, incorrect configuration, or a failed communication module.

## 3. Controller Status LEDs

LEDs provide a quick indication of the controller's operating state without requiring a programming computer.

Common labels include RUN, OK, ERR, FAULT, SF, BF, I/O, and COMM. The exact labels, colors, blink patterns, and meanings depend on the manufacturer and controller model.

Illustrative PLC front-panel indicators

+------------------------------------+

|             PLC CPU                |

|                                    |

|  [ RUN ]   Green / Status          |

|  [ ERR ]   Red / Error             |

|  [ I/O ]   Module or I/O Status    |

|  [ COMM ]  Communication Status    |

|                                    |

|  PORT 1             PORT 2         |

+------------------------------------+

This is a conceptual illustration, not a model-specific LED map.

### Common LED interpretations

| Indicator | Possible meaning | What to check |
| --- | --- | --- |
| RUN | Controller is executing its program | Confirm the expected operating mode |
| STOP | Controller is not executing normal logic | Check operating mode and stop cause |
| ERR or FAULT | Controller or program fault | Read the fault details and diagnostic records |
| SF | System fault on some platforms | Inspect CPU, module, or system diagnostics |
| BF | Bus fault on some platforms | Inspect network configuration and connected devices |
| I/O | I/O status or module fault, depending on platform | Check module and channel diagnostics |
| COMM | Communication activity or status, depending on platform | Check device connection and network diagnostics |

Important: An LED's meaning must be verified against the exact controller manual. The same label does not guarantee the same behavior across manufacturers.

### Steady versus flashing LEDs

A steady indicator may represent a persistent state, while a flashing indicator may represent a specific fault, startup condition, or communication state.

Do not assume that flashing always means a fault. Record the exact LED label, color, and blink pattern before consulting the relevant manual.

## 4. Diagnostic Buffer

A diagnostic buffer is a controller-maintained record of diagnostic events, faults, warnings, and operating-state changes.

Depending on the platform, it may include:

CPU startup and restart events.

Controller mode changes.

I/O module faults.

Communication interruptions.

Program or execution errors.

Configuration inconsistencies.

Power-related events.

Module insertion, removal, or recovery events.

The diagnostic buffer is especially useful for intermittent problems because it may preserve evidence of an event that is no longer active.

### Example diagnostic sequence

Imagine a production station stops at 14:32.

| Time | Event |
| --- | --- |
| 14:31:58 | Remote I/O connection interrupted |
| 14:32:00 | Production sequence stops |
| 14:32:03 | Device communication fault recorded |
| 14:32:12 | Communication restored |
| 14:32:15 | Operator reports that the station is stopped |

The operator sees a stopped station, but the diagnostic history indicates that communication was interrupted first.

The timing suggests a possible relationship, but further investigation is still required to establish the root cause.

### How to inspect a diagnostic buffer

1.	Connect to the correct PLC using the approved engineering software.

2.	Confirm the controller identity and operating state.

3.	Open the controller's diagnostic or event-buffer view.

4.	Record the event timestamp, identifier, description, and affected component.

5.	Inspect the events immediately before and after the failure.

6.	Compare the recorded events with the machine sequence and operator observations.

7.	Preserve the evidence before clearing or resetting anything.

The exact menu names differ between engineering environments.

### Why event order matters

A fault recorded after a machine stops may be a consequence rather than the original cause.

For example:

Network Connection Lost

|

v

Remote I/O Data Becomes Unavailable

|

v

Sequence Cannot Continue

|

v

Machine Stops

The network fault is a candidate initiating event. The machine stop is a resulting symptom.

This distinction is essential when preparing root-cause analysis reports.

## 5. Fault Codes and Error Messages

A fault code is an identifier associated with a detected error or abnormal condition. The corresponding message or diagnostic details explain what the controller detected.

Fault information may include:

Error code or identifier.

Fault description.

Affected module, task, instruction, or channel.

Timestamp.

Fault location or program context.

Additional status or diagnostic data.

Suggested corrective checks.

There is no universal PLC fault-code list. A code from one manufacturer, CPU family, or software version may mean something entirely different on another platform.

### Fault categories

| Category | Example | First area to investigate |
| --- | --- | --- |
| CPU/system fault | Controller enters a fault state | CPU diagnostics and execution records |
| Program fault | Invalid instruction execution or execution error | Program location and relevant data |
| I/O fault | Module or channel reports an error | Module status, wiring, configuration |
| Communication fault | Connection to a remote device is lost | Network, device power, connection configuration |
| Configuration fault | Hardware configuration does not match the installed system | Hardware configuration and module identity |
| Process/application fault | Cylinder fails to reach its expected position | Sensor feedback, sequence conditions, actuator |
| Safety-related fault | Safety condition prevents operation | Approved safety diagnostics and safety-system documentation |

### Fault versus alarm

These terms are related but not interchangeable.

| Fault | Alarm |
| --- | --- |
| Indicates an abnormal or failed condition | Notifies an operator of a condition requiring attention |
| May affect controller operation or machine availability | May be informational, warning-level, or stop-related |
| May be generated by the CPU, module, or application | Often generated by application logic or an HMI |
| Can exist without a dedicated operator alarm | Can exist without a controller-level fault |

For example, a PLC may be operating normally while an HMI displays a CLAMP EXTEND TIMEOUT alarm. The application has detected that a process condition was not met, but the CPU itself may have no execution fault.

## 6. Diagnostic Information from I/O Modules

I/O diagnostics help determine whether a problem exists at the module level, the channel level, or further downstream in the field circuit.

### Digital input example

A sensor is physically detecting a component, but the PLC input tag remains FALSE.

Investigate the signal path in order:

Component

|

v

Sensor Detects Component

|

v

Sensor Output

|

v

Field Wiring and Supply

|

v

Input Module Channel

|

v

PLC Input Data

|

v

Program Tag and Logic

At each stage, ask what evidence confirms that the signal has reached that point.

| Observation | Possible interpretation |
| --- | --- |
| Sensor indicator is OFF | Detection, sensor supply, or sensor configuration issue |
| Sensor indicator is ON, PLC channel is OFF | Wiring, electrical compatibility, or input-channel issue |
| Input channel is ON, PLC tag is OFF | Mapping, addressing, update, or tag-selection issue |
| PLC tag is ON, output command is OFF | Logic conditions, interlocks, permissives, or sequence state |
| Output command is ON, actuator does not operate | Output module, circuit, supply, valve, or actuator issue |

These are diagnostic clues, not automatic conclusions. Confirm each one through appropriate measurements and controller diagnostics.

### Analog input example

A pressure transmitter should report a valid pressure, but the PLC value is zero or outside the expected range.

Check:

Transmitter supply and wiring.

Signal type and range, such as 4 to 20 mA or 0 to 10 V.

Input module configuration.

Channel diagnostics and wire-break detection, if supported.

Raw input value and engineering-unit scaling.

Program logic and any range checks.

Do not assume that an analog value of zero means the physical pressure is zero. It could indicate a configuration, wiring, scaling, or signal problem.

## 7. Communication Diagnostics

Modern automation systems often depend on communication between PLCs, remote I/O, robots, drives, HMIs, and supervisory systems.

Communication diagnostics can help identify:

Lost or interrupted connections.

Device timeouts.

Configuration mismatches.

Addressing problems.

Network congestion or excessive update delays.

Device power loss.

Cable, connector, or switch faults.

A communication fault may affect only one device or an entire group of devices, depending on the network architecture.

### Example: Remote I/O fault

Suppose several sensors connected to one remote I/O station stop updating simultaneously, while sensors on the local PLC rack continue working.

This pattern suggests investigating the shared remote I/O path before testing every sensor individually.

Check the remote station's power, network link, connection status, module diagnostics, and controller-side connection records.

If multiple unrelated signals fail together, look for a shared cause.

## 8. Program-Level Diagnostics

Not every machine stoppage creates a CPU fault. Many important failures are detected and handled by the application program.

Examples include:

A timer expires before a cylinder reaches its end position.

A robot-ready signal is missing.

A permissive condition is not satisfied.

A sequence step does not receive the expected feedback.

A drive reports a fault through a PLC tag.

A part-presence signal contradicts another sensor.

### Example: Cylinder extension timeout

Command Cylinder Extend

|

v

Wait for Extended Sensor

|

+---- Sensor ON ----> Continue Sequence

|

+---- Timeout -----> Set Alarm

Stop or Hold Sequence

If the timeout alarm activates, investigate both the logic and the physical system.

Possible causes include a failed sensor, a disconnected wire, low pneumatic pressure, a stuck valve, mechanical obstruction, incorrect timer settings, or a sequencing issue.

The alarm identifies the failed expectation. It does not prove which component caused it.

## 9. Systematic PLC Fault-Troubleshooting Procedure

Use this sequence when investigating a real fault.

### Step 1: Establish the condition

Record the machine state, fault time, affected station, operating mode, and what the equipment was doing immediately before the stop.

### Step 2: Check controller status

Observe the CPU operating state and all relevant status indicators. Record exact LED labels, colors, and blink patterns.

### Step 3: Read diagnostic information

Inspect the controller diagnostic buffer, module diagnostics, network status, and relevant program messages.

### Step 4: Identify the first abnormal event

Compare timestamps and event order. Determine which abnormal condition occurred first, rather than focusing only on the final alarm.

### Step 5: Trace the signal path

For an input problem, trace from the sensor to the PLC tag. For an output problem, trace from the program command to the physical actuator.

### Step 6: Verify the suspected cause

Use approved measurements, engineering diagnostics, wiring diagrams, and component documentation. Distinguish confirmed findings from assumptions.

### Step 7: Correct and validate

Follow the site's isolation, safety, change-control, and restart procedures. Confirm that the original function works and that no related faults remain.

### Step 8: Record the result

Document the symptom, root cause, corrective action, verification, and any preventive action needed to reduce recurrence.

## 10. Common Troubleshooting Mistakes

| Mistake | Why it is a problem | Better approach |
| --- | --- | --- |
| Resetting the PLC immediately | Can remove useful evidence or change the observed condition | Record the fault and diagnostic history first |
| Replacing a module based only on an LED | The fault may originate in wiring, power, or configuration | Confirm the diagnosis using module and field measurements |
| Assuming every machine stop is a CPU fault | Process interlocks and missing feedback can stop a machine without a CPU fault | Check application and field-device conditions |
| Looking only at the latest event | The latest event may be a consequence | Review the preceding event sequence |
| Clearing faults before recording them | May destroy or obscure useful troubleshooting evidence | Preserve relevant records first |
| Forcing an input or output to test it | Can bypass normal logic and create unexpected machine movement | Use approved test procedures and risk controls |
| Increasing timers without identifying the cause | Can hide a real mechanical or electrical problem | Verify the physical process and timing requirements |
| Assuming a fault code is universal | Codes vary by platform and version | Use the correct manufacturer documentation |

## 11. Diagnostic Buffer, LED, and Fault Code: How They Work Together

These three tools provide different kinds of evidence.

| Tool | Primary purpose | Limitation |
| --- | --- | --- |
| LEDs | Rapid indication of controller or module status | Often insufficient to identify the root cause |
| Diagnostic buffer | Records diagnostic events and their sequence | Records depend on what the platform captures and retains |
| Fault codes and messages | Identify a specific detected condition | A code may identify the symptom without proving the underlying cause |

For example, a red fault LED tells you that a fault condition exists. The diagnostic buffer may show when it began. The fault details may identify the affected remote I/O connection. Network and module checks can then establish whether the cause is power, wiring, configuration, or hardware.

The strongest diagnosis combines all three with direct verification.

## 12. Manufacturer-Specific Considerations

| Platform | General diagnostic approach |
| --- | --- |
| Siemens SIMATIC | Inspect CPU and module diagnostic information, diagnostic buffers, status LEDs, and online diagnostics in the applicable engineering software |
| Rockwell Automation Logix | Inspect controller faults, module and connection status, task or program faults, and relevant diagnostic information in the engineering environment |
| Mitsubishi MELSEC | Inspect CPU error information, module status, diagnostic records, and communication-related information using the applicable engineering software |

The exact menus, terminology, fault identifiers, and recovery procedures depend on the controller family, firmware, and software version.

Use the manufacturer's manual for the specific hardware installed on the machine. Never apply a reset or recovery procedure solely because it worked on a different PLC model.

## 13. Interview Questions and Answers

Q1. What is PLC diagnostics?

The process of identifying and analyzing faults using controller status, diagnostic records, fault codes, module information, communication status, and application-level information.

Q2. What is a diagnostic buffer?

A controller-maintained record of diagnostic events, faults, warnings, and operating-state changes, subject to the capabilities and retention behavior of the PLC.

Q3. What information can a PLC status LED provide?

It can indicate operating state, system fault, communication status, or module condition. Exact meanings depend on the controller model and LED pattern.

Q4. What is a fault code?

An identifier associated with a detected abnormal condition. Its meaning must be interpreted using the correct manufacturer's documentation.

Q5. Why should the diagnostic buffer be checked before resetting a PLC?

Because it may contain evidence about the original fault, including event order, timestamps, and affected components.

Q6. Can a PLC stop a machine without having a CPU fault?

Yes. The application may stop a sequence because an interlock, permissive, safety condition, or process feedback requirement is not satisfied.

Q7. What is the difference between a fault and its root cause?

The fault is the detected abnormal condition. The root cause is the underlying reason that produced it. A communication fault, for example, may be caused by a failed cable or loss of device power.

Q8. Why is the first abnormal event important?

It can help distinguish the initiating failure from later alarms and secondary consequences.

Q9. What should be checked when multiple I/O signals fail simultaneously?

Investigate shared components such as the remote I/O station, power supply, network connection, common wiring, or communication configuration.

Q10. Should a fault always be reset immediately?

No. Record and investigate the fault first, then follow the approved recovery procedure. Resetting without understanding the cause may conceal evidence or allow the fault to recur.

## 14. Practical Study Exercise

Use an approved engineering environment or an available training PLC. Do not create faults on a running production machine merely to practise diagnostics.

Record the following:

| Item | What to document |
| --- | --- |
| Controller identity | Manufacturer, model, firmware |
| Controller status | RUN/STOP state and relevant LEDs |
| Diagnostic event | Exact message and fault identifier |
| Event time | Timestamp and sequence of related events |
| Affected device | CPU, module, channel, network node, or application |
| Signal evidence | Relevant input, output, or status tag |
| Suspected cause | Initial hypothesis based on evidence |
| Verification | Test or diagnostic result supporting or rejecting the hypothesis |
| Corrective action | Repair, configuration correction, or approved recovery |
| Final validation | Confirmation that the function operates correctly |

The objective is to learn how to move from a fault indication to a verified diagnosis, with enough recorded evidence that another engineer can understand and reproduce the reasoning.

## 15. Final Mental Model

LEDs: Show an immediate status indication.

Diagnostic buffer: Shows recorded events and their sequence.

Fault codes: Identify detected error conditions.

Module diagnostics: Narrow the problem to a device, channel, or connection.

Program diagnostics: Reveal missing conditions and sequence failures.

Root-cause analysis: Establishes why the failure occurred.

Validation: Confirms that the corrective action actually solved the problem.

The core principle is simple: observe, record, isolate, verify, correct, and validate. Good diagnostics turns an unexpected machine stop into a structured technical investigation.

# Next Topic: 01_Ladder

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\04_Programming\01_Ladder

Topic: Ladder Logic (Ladder Diagram)

This topic will introduce the ladder-logic programming model, including rails and rungs, contacts, coils, Boolean logic, execution order, and how to read industrial PLC programs.