# 01. Ladder Logic (Ladder Diagram)

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\04_Programming\01_Ladder

Ladder Diagram, commonly called Ladder Logic or LD, is a graphical PLC programming language used to implement industrial control logic.

It represents control conditions using symbols arranged in horizontal rungs between two conceptual power rails. The symbols represent logical operations, Boolean conditions, output commands, timers, counters, and other control instructions.

Ladder logic became popular because its structure resembles traditional electrical relay-control circuits. This makes it relatively easy for electrical and maintenance engineers to read, troubleshoot, and understand machine-control behavior.

However, ladder logic is not simply an electrical schematic drawn on a screen. It is an executable program whose instructions are evaluated according to the PLC's execution rules.

## 1. Why Ladder Logic Is Used

Consider a machine where a motor should start when the operator presses START, provided that the safety conditions are satisfied and the motor is not faulted.

The control requirements might be:

The motor must be permitted to run.

The operator must request a start.

The motor command must remain active after the START button is released.

Pressing STOP or detecting a fault must stop the motor.

These requirements can be represented using ladder logic.

The major advantage is that an engineer can trace the conditions leading to an output command without translating every operation into a textual programming language.

Typical applications include:

Motor start/stop circuits.

Conveyor sequencing.

Robot handshakes.

Pneumatic and hydraulic equipment.

Interlocks and permissives.

Machine cycle control.

Timers, counters, and alarms.

Automated assembly and welding stations.

## 2. Basic Ladder Diagram Structure

A traditional ladder diagram uses two vertical rails and horizontal rungs.

Left Rail                         Right Rail

|                                  |

|----[ Condition A ]----( Output )-|

|                                  |

|----[ Condition B ]----( Alarm )--|

|                                  |

The rails and rungs provide a visual structure for the program. They are not normally physical wires carrying electrical power through the software.

| Element | Meaning |
| --- | --- |
| Left rail | Conventional starting side of a rung |
| Right rail | Conventional ending side of a rung |
| Rung | A logical network of instructions |
| Contact instruction | Tests a Boolean condition |
| Coil instruction | Writes or controls a Boolean result |
| Branch | Represents parallel logical paths |
| Tag or address | Identifies the data used by an instruction |

In many PLC environments, a program consists of multiple routines, each containing several rungs or networks.

## 3. Basic Ladder Instructions

### A. Normally Open Contact Instruction

A normally open, or NO, contact instruction is commonly represented as:

----[ ]----

In basic Boolean terms, it is TRUE when the referenced Boolean value is TRUE.

For example:

----[ START_PB ]----

If START_PB = TRUE, the instruction evaluates as TRUE. If START_PB = FALSE, it evaluates as FALSE.

Important: The instruction tests a program value. It does not physically open or close an electrical contact inside the PLC.

### B. Normally Closed Contact Instruction

A normally closed, or NC, contact instruction is commonly represented as:

----[/]----

It evaluates as TRUE when the referenced Boolean value is FALSE.

For example:

----[/ MOTOR_FAULT ]----

If MOTOR_FAULT = FALSE, the instruction evaluates as TRUE. If MOTOR_FAULT = TRUE, it evaluates as FALSE.

The NO and NC symbols describe the logical test performed by the instruction. They do not necessarily describe the physical construction or normal state of the field device.

### C. Output Coil Instruction

A common output coil representation is:

----( )----

For a basic coil instruction, the PLC writes a Boolean result based on the rung's logical condition.

For example:

----[ MOTOR_PERMIT ]----( MOTOR_CMD )

If MOTOR_PERMIT is TRUE, the rung condition is TRUE and the coil writes TRUE to MOTOR_CMD. Otherwise, the coil writes FALSE.

The exact behavior of specialized coil instructions differs between PLC platforms.

## 4. Boolean Logic in Ladder

Ladder logic implements Boolean operations through the arrangement of contacts, branches, and instructions.

### A. AND Logic: Series Contacts

When contacts are placed in series, all conditions must evaluate as TRUE for the path to be TRUE.

----[ A ]----[ B ]----( Y )

The Boolean expression is:

Y=A∧B

| A | B | Y |
| --- | --- | --- |
| 0 | 0 | 0 |
| 0 | 1 | 0 |
| 1 | 0 | 0 |
| 1 | 1 | 1 |

Example: A conveyor may run only when START_REQUEST is TRUE and MOTOR_PERMIT is TRUE.

### B. OR Logic: Parallel Branches

When conditions are placed on parallel branches, either branch can establish a TRUE logical path.

+----[ A ]----+

----+-----|             |----( Y )

|     +----[ B ]----+

The Boolean expression is:

Y=A∨B

| A | B | Y |
| --- | --- | --- |
| 0 | 0 | 0 |
| 0 | 1 | 1 |
| 1 | 0 | 1 |
| 1 | 1 | 1 |

Example: A conveyor may receive a run request from either the local control station or an authorized automatic sequence.

### C. NOT Logic: Inverted Condition

A logically inverted condition can be represented using an NC contact instruction.

----[/ A ]----( Y )

The expression is:

Y=¬A

| A | Y |
| --- | --- |
| 0 | 1 |
| 1 | 0 |

Example: A NOT FAULT condition may be used as one of several requirements for a motor-run command.

Remember that the logical inversion applies to the referenced Boolean value, not necessarily to the physical sensor's electrical behavior.

## 5. Combining AND, OR, and NOT

Industrial programs combine these operations to express machine conditions.

Suppose a motor can run when:

Automatic mode is selected, or a local manual-run request is active.

The motor is permitted to operate.

No motor fault is present.

The Boolean expression is:

MOTORCMD=(AUTO∨MANUAL)∧PERMIT∧¬FAULT

A conceptual ladder representation is:

+----[ AUTO ]------+

|                  |

----+-----+                  +----[ PERMIT ]----[/ FAULT ]----( MOTOR_CMD )

|     |                  |

|     +----[ MANUAL ]----+

The parallel branch implements OR logic. The series conditions after the branch implement AND logic.

This is a fundamental skill in reading industrial programs: translate the rung into a Boolean expression, then verify whether that expression matches the intended machine behavior.

## 6. Physical Devices Versus Ladder Instructions

One of the most important distinctions in PLC programming is the difference between a physical device and the logical representation of that device.

| Physical device or condition | Example PLC representation |
| --- | --- |
| Push button | START_PB |
| Proximity sensor | PART_PRESENT |
| Motor overload feedback | MOTOR_FAULT |
| Drive-ready feedback | DRIVE_READY |
| Internal sequence state | STEP_10_ACTIVE |
| Motor command | MOTOR_CMD |

The tag name is meaningful only if its mapping and intended behavior are understood.

For example, a physical normally closed stop contact may be wired so that the PLC input is TRUE when the circuit is healthy. An NO ladder instruction testing that healthy-state tag could be appropriate.

Conversely, an NC ladder instruction could be used to test the same tag's FALSE state.

Therefore, never infer the electrical wiring solely from the NO or NC symbol displayed in the ladder program.

## 7. Latching and Start/Stop Logic

A common ladder-logic application is a motor start/stop circuit in which the run command remains active after the START button is released.

A simplified conceptual example is:

----[/ STOP_REQUEST ]----[/ MOTOR_FAULT ]----+----[ START_PB ]----+----( MOTOR_CMD )

|                    |

+----[ MOTOR_CMD ]---+

The MOTOR_CMD contact creates a holding path. Once the command becomes TRUE, that path can maintain the command after the start request returns to FALSE.

The logical expression is:

MOTORCMD=¬STOPREQUEST∧¬MOTORFAULT∧(STARTPB∨MOTORCMDprevious)

This equation describes the simplified holding behavior. Actual program behavior depends on execution order, tag-writing rules, and any additional conditions in the complete application.

### How it operates

1.	Initially, MOTOR_CMD is FALSE.

2.	The operator presses START, making START_PB TRUE.

3.	The rung becomes TRUE, and the coil writes TRUE to MOTOR_CMD.

4.	The holding contact now evaluates TRUE.

5.	When START is released, the holding path keeps the command TRUE.

6.	When STOP is requested or the fault condition becomes TRUE, the rung becomes FALSE and the command drops out.

This is a software latch formed through feedback in the logic.

Safety note: This example is for understanding standard control logic, not for designing a safety-rated stop circuit. Emergency stops and other safety functions must use the appropriate validated safety architecture. A normal PLC rung must not be treated as a substitute.

## 8. Ladder Execution Order and Scan Behavior

Ladder instructions execute according to the PLC's program organization and execution rules.

In a typical cyclic program, the controller processes instructions in a defined order. A result written by one instruction may affect a later instruction during the same execution cycle.

Consider:

Rung 1:

----[ START_PB ]----------------( RUN_CMD )

Rung 2:

----[ RUN_CMD ]-----------------( RUN_INDICATOR )

In a common sequential execution model, if Rung 1 writes RUN_CMD = TRUE, Rung 2 may read the updated value during the same program execution.

However, exact execution and data-update behavior depends on the PLC platform, task model, and instruction type.

### Multiple writes to the same tag

Consider:

Rung 1:

----[ CONDITION_A ]-------------( MOTOR_CMD )

Rung 2:

----[ CONDITION_B ]-------------( MOTOR_CMD )

If both are ordinary output coil instructions writing the same tag, the later executed write may overwrite the earlier result. If CONDITION_A is TRUE but CONDITION_B is FALSE, the final value may therefore be FALSE.

This behavior can create difficult faults when a tag has multiple writers.

Good programming practice is to establish clear ownership of command tags, use consistent set/reset patterns where appropriate, and inspect all writes to a tag when diagnosing unexpected behavior.

## 9. Ladder Instructions Beyond Contacts and Coils

Ladder programming includes many instruction types beyond simple Boolean logic.

| Instruction category | Purpose | Example application |
| --- | --- | --- |
| Contacts and coils | Evaluate and write Boolean states | Motor control |
| Set/reset or latch/unlatch | Maintain or clear a state | Sequence-state memory |
| Timers | Measure elapsed time | Cylinder timeout |
| Counters | Count events | Part counting |
| Comparisons | Compare numeric values | Pressure threshold |
| Arithmetic | Perform numeric calculations | Speed or position calculations |
| Move/data transfer | Copy values between tags | Data handling |
| One-shot instructions | Detect an event or transition | Count a rising-edge event |
| Shift registers and arrays | Manage structured data | Part tracking |
| Program control | Organize or conditionally execute logic | Sequence routines |

Instruction names and exact behavior differ across platforms. Some instructions are standard concepts but not identical implementations.

## 10. Timers in Ladder Logic

A timer is often used to delay an action or monitor how long a condition remains active.

For example, a machine may declare a cylinder-extension timeout if the extended-position sensor does not activate within a specified interval.

----[ EXTEND_COMMAND ]---------[ TON EXTEND_TIMER ]

Conceptually, a typical on-delay timer behaves as follows:

When the enabling condition becomes TRUE, timing begins.

When the preset time is reached, the timer's completion status becomes TRUE.

When the enabling condition becomes FALSE, the timer generally resets in a conventional non-retentive on-delay implementation.

The precise reset behavior depends on the timer type and PLC platform.

A timeout alarm could then use the timer's completion status together with the missing feedback condition.

----[ EXTEND_TIMER.DONE ]----[/ EXTENDED_SENSOR ]----( EXTEND_TIMEOUT )

This is a simplified conceptual example. The real program must also handle command cancellation, sensor transitions, sequence state, reset behavior, and safe recovery.

## 11. Common Ladder Logic Errors

| Error | Possible result | What to inspect |
| --- | --- | --- |
| Incorrect series/parallel arrangement | Wrong AND/OR behavior | Trace the logical path |
| Incorrect NO/NC instruction | Condition evaluated in the wrong state | Verify the tag's meaning and expected Boolean value |
| Multiple writers to a tag | Unexpected final value | Search for every instruction that writes the tag |
| Missing holding logic | Command drops when the request disappears | Inspect latch or feedback conditions |
| Incorrect timer reset behavior | Timer remains done or resets unexpectedly | Verify timer type and enabling conditions |
| Incorrect tag mapping | Program uses the wrong physical signal | Check I/O configuration and symbolic mapping |
| Wrong execution assumptions | Later logic reads a different value than expected | Inspect task organization and execution order |
| Missing interlock or permissive | Machine may execute an unintended sequence | Review functional requirements and approved design |
| Poor tag naming | Troubleshooting takes longer | Use clear, consistent naming conventions |

## 12. How to Read an Existing Ladder Program

When investigating an unfamiliar machine, follow this order.

1.	Identify the output or command involved in the symptom.

2.	Find the rung or instruction that writes that tag.

3.	Trace each series condition and parallel branch.

4.	Check the live state of each referenced tag using approved monitoring tools.

5.	Determine which condition is preventing the expected result.

6.	Check whether another rung or routine also writes the same tag.

7.	Trace the physical input or output mapping if the tag does not match the field condition.

8.	Verify the result against the machine sequence and functional requirements.

For example, if a robot is not receiving a start command, begin with the PLC tag that sends the command. Trace its rung conditions, robot-ready signal, interlocks, sequence state, and communication mapping.

Do not start by changing the logic. First establish which condition is preventing the command and why.

## 13. Ladder Logic and Electrical Schematics

Although ladder logic resembles relay diagrams, they represent different things.

| Electrical schematic | Ladder program |
| --- | --- |
| Represents electrical connections and components | Represents executable control instructions |
| Shows physical contacts, coils, wiring, and circuit paths | Shows logical conditions, data, and commands |
| Electrical behavior depends on wiring and component characteristics | Execution depends on PLC instructions and scheduling |
| Fault tracing often involves voltage, current, continuity, and wiring | Fault tracing also involves tags, program state, and execution order |
| A relay coil physically energizes or de-energizes | A ladder coil instruction writes or updates a program value |

In a real machine, both views are necessary. The PLC program explains the intended control decision, while the electrical drawings and measurements help establish what is happening in the physical circuit.

## 14. Interview Questions and Answers

Q1. What is Ladder Logic?

A graphical PLC programming language that represents control operations using contacts, coils, branches, and other instructions arranged in rungs.

Q2. What does a normally open ladder contact do?

It evaluates as TRUE when the referenced Boolean value is TRUE.

Q3. What does a normally closed ladder contact do?

It evaluates as TRUE when the referenced Boolean value is FALSE.

Q4. How is AND logic represented?

Typically, by placing logical conditions in series.

Q5. How is OR logic represented?

Typically, by placing conditions on parallel branches.

Q6. Is a ladder contact symbol the same as a physical electrical contact?

No. A ladder contact instruction tests a program value. The physical device and its wiring must be understood separately.

Q7. What is a holding circuit?

A control arrangement that maintains a command after the original request disappears, usually through a feedback path or latch instruction.

Q8. Why can multiple output coils writing the same tag cause problems?

Because the final value may depend on execution order and the instructions used. Later writes can overwrite earlier results.

Q9. What is the purpose of a timer in ladder logic?

To measure elapsed time or implement time-based behavior, such as delays, sequence timing, and process timeouts.

Q10. What is the first step when a ladder-controlled output does not turn on?

Identify the command tag and trace the rung conditions that determine its state, then verify the relevant input, interlock, permissive, and mapping information.

## 15. Practical Study Exercise

Using an offline PLC simulator, training project, or approved non-production environment, create a basic motor-command rung.

Requirements:

START_PB requests a start.

STOP_REQUEST stops the command.

MOTOR_FAULT prevents operation.

MOTOR_CMD remains TRUE after START is released, until STOP is requested or a fault occurs.

Test the following conditions:

| START_PB | STOP_REQUEST | MOTOR_FAULT | Expected behavior |
| --- | --- | --- | --- |
| FALSE | FALSE | FALSE | Remain stopped if no prior latch exists |
| TRUE | FALSE | FALSE | Start command becomes TRUE |
| FALSE | FALSE | FALSE | Command remains TRUE if the holding path is active |
| FALSE | TRUE | FALSE | Command becomes FALSE |
| TRUE | FALSE | TRUE | Command must remain FALSE under the stated requirements |

Observe the Boolean values and execution behavior. Then identify how the same functional requirements would be implemented using the instructions and conventions of your particular PLC platform.

Do not test modified start/stop logic on live machinery without the approved engineering, safety, and commissioning process.

## 16. Final Mental Model

Rungs organize control logic.

Contacts test Boolean conditions.

Coils write or update Boolean results.

Series paths commonly implement AND logic.

Parallel branches commonly implement OR logic.

Inverted contacts implement NOT logic on a referenced value.

Timers and counters introduce time-based and event-counting behavior.

Execution order determines how program values are evaluated and updated.

Tag mapping connects program logic to the physical automation system.

The most useful skill is not memorizing symbols. It is being able to translate a rung into a logical statement, predict its result for different input states, and trace that result through to the physical machine.

# Next Topic: 02_Function_Blocks

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\04_Programming\02_Function_Blocks

Topic: Function Blocks

The next topic will cover reusable control logic, function blocks and function-block instances, inputs and outputs, retained internal state, and how function blocks differ from ordinary functions and ladder rungs.