# 04_Backup_Restore: Backup & Restore, Save Project and Restore CPU

## 1. Definition

PLC backup and restoration is the process of preserving the information required to recover a control system after hardware failure, program corruption, accidental changes, project loss or controller replacement.

A backup is a recoverable copy of the engineering project, controller program and other required configuration information. Restoration is the controlled process of returning the controller and associated system to an approved working state.

The objective is not merely to save a PLC program. It is to preserve enough verified information to recover the intended machine behavior.

For industrial maintenance, this is essential because a replacement CPU may be available immediately, while the correct program, firmware, configuration and commissioning records may not be.

## 2. Why PLC Backup and Restore Matter

Common situations requiring backup or restoration include:

PLC CPU failure.

Memory-card or storage failure.

Accidental program deletion or overwrite.

Incorrect download or online modification.

Corrupted engineering project.

Controller replacement during maintenance.

Firmware upgrade or hardware migration.

Recovery after an electrical event or other equipment failure.

Vendor changes that were not incorporated into the master project.

Loss of the engineering computer or original project files.

A controller may be replaceable in a few hours, but recovery can take much longer if the correct project and configuration are unavailable.

Maintenance principle: The real asset is not only the PLC hardware. It is the verified, documented and recoverable control-system configuration.

## 3. Backup vs Upload vs Save vs Restore

These operations are related but different.

| Operation | Meaning | Purpose |
| --- | --- | --- |
| Save project | Save the engineering project to storage. | Preserve the current local engineering work. |
| Upload | Retrieve supported information from the PLC to the engineering computer. | Recover or inspect controller contents. |
| Backup | Preserve a recoverable copy of the required project and configuration. | Enable recovery after loss or failure. |
| Restore | Use a suitable backup or approved source to recover the system. | Return the controller or system to an approved state. |
| Download | Transfer an engineering project or supported configuration to the PLC. | Deploy the selected project. |
| Compare | Check supported differences between versions. | Confirm which version is present and identify changes. |
| Archive | Store a controlled, identifiable snapshot of project information. | Maintain traceability and historical revisions. |

Saving a file is not necessarily a complete backup. Uploading from the PLC does not necessarily recover all source documentation. Downloading a backup does not automatically restore every part of the physical control system.

## 4. What Should Be Backed Up?

A complete recovery package depends on the controller family and the machine's architecture. The following categories should be assessed.

| Backup item | What it preserves | Why it matters |
| --- | --- | --- |
| Engineering project | Program, tags, routines and supported project structure. | Reconstructs the intended control logic. |
| Hardware configuration | CPU, rack, I/O modules and device configuration. | Helps recreate the expected hardware arrangement. |
| Controller parameters | Supported CPU and application parameters. | May be required to restore the intended behavior. |
| Firmware information | Installed firmware and compatibility details. | Helps select a compatible replacement or engineering environment. |
| Network configuration | IP addresses, communication paths and device addressing. | Restores communication with connected systems. |
| Drive configuration | Drive parameters and approved configuration files, where applicable. | Helps restore motor-control behavior. |
| Robot configuration | Relevant controller programs and configuration, where applicable. | Supports recovery of integrated robotic systems. |
| HMI / SCADA project | Operator screens, tags, alarms and communication configuration. | Restores operator interaction and supervisory monitoring. |
| Safety-related project and records | Supported safety project data, signatures or validation information as applicable. | Supports controlled restoration and required safety validation. |
| Libraries and dependencies | External libraries, add-ons and required engineering assets. | Avoids missing dependencies during recovery. |
| Documentation | I/O lists, tag descriptions, network diagrams and change records. | Helps engineers verify and maintain the restored system. |
| Version history | Approved revisions and descriptions of changes. | Establishes which project is authoritative. |

A machine with PLCs, robots, drives, HMIs, remote I/O and SCADA may need multiple coordinated backups. A PLC project alone may not restore the complete machine.

## 5. Types of Backup

### 5.1 Engineering project backup

This is the native project file saved by the engineering software.

Examples include:

Rockwell Studio 5000 Logix Designer project files.

Siemens STEP 7 or TIA Portal project files.

Mitsubishi GX Works2 or GX Works3 project files.

The native project is generally the primary engineering artifact because it can preserve source-level information that may not be recoverable from the controller alone.

### 5.2 Controller-resident backup

Some controllers support memory cards, removable storage, nonvolatile memory or other mechanisms for retaining programs and configuration.

The stored contents and recovery behavior vary by controller family. A memory card is not automatically a complete, current backup of every engineering asset.

### 5.3 Full engineering recovery package

A recovery package combines the native project with the supporting information needed to restore the intended system.

For example:

FR1010_PLC_RECOVERY/

Engineering_Project/

Firmware_And_Versions/

Hardware_Configuration/

Network_Configuration/

I_O_And_Tag_Lists/

HMI_And_SCADA/

Drive_And_Robot_Assets/

Safety_Records/

Change_History/

Restore_Procedure/

Validation_Records/

This is an illustrative folder structure. The actual contents should match the machine's architecture and site requirements.

### 5.4 Full-system backup

For a complex production line, the backup scope may extend beyond the PLC to include:

Engineering workstations and software versions.

HMI and SCADA computers.

Industrial PCs.

Databases and relevant application configurations.

Network and switch configurations.

Robot controllers.

CNC systems.

Drives and motion controllers.

License information and required installation media.

Not every item should be copied in the same way. Databases, software licenses, encrypted configurations and safety-related assets may require their own supported backup procedures.

## 6. What Makes a Backup Reliable?

A backup is useful only if it is identifiable, complete enough for its intended purpose and recoverable.

A reliable backup should have the following properties.

| Property | Requirement |
| --- | --- |
| Correct identity | Machine and controller are clearly identified. |
| Known revision | Project version and backup date are recorded. |
| Compatibility | Controller model, firmware and engineering-software requirements are documented. |
| Completeness | Required programs, configuration and dependencies are included. |
| Integrity | The stored files can be opened or otherwise validated using the supported method. |
| Traceability | Author, reason for change and approval information are recorded. |
| Security | Access is controlled, and sensitive configuration is protected. |
| Separation | Backup is stored independently of the equipment it protects. |
| Recoverability | The restore procedure is known and can be tested safely. |
| Verification | The backup has been checked according to the site's recovery requirements. |

A folder containing a file named FINAL_PLC_PROJECT_NEW is not evidence of a reliable backup. Humans have an impressive ability to create filenames that communicate absolutely nothing.

## 7. Recommended Backup Workflow

### Step 1: Identify the equipment

Record the machine, line, controller model, controller identity, firmware, software version and relevant network information.

### Step 2: Establish the authoritative project

Confirm which project corresponds to the approved controller program. If the local project and PLC differ, investigate the difference before overwriting either copy.

### Step 3: Save the project

Save the native engineering project and create a separate revision for the backup. Avoid replacing the only known-good file.

### Step 4: Capture supporting configuration

Preserve the required hardware configuration, network settings, I/O mapping, device parameters, HMI or SCADA assets and other dependencies.

Use manufacturer-supported export or backup mechanisms where available.

### Step 5: Record controller information

Record the CPU model, firmware, operating mode, fault state and any relevant memory-card or nonvolatile-storage configuration.

### Step 6: Validate the backup

Check that the files are present and readable. Open the project in a compatible engineering environment where practical. Review any warnings or missing dependencies.

A project opening successfully does not prove that every component of the machine can be restored, but it is a useful verification step.

### Step 7: Store the backup securely

Store the backup in an approved location independent of the controller and its local engineering computer.

Maintain appropriate access controls and additional copies according to site policy.

### Step 8: Record the restore procedure

Document the steps, required software, compatible hardware, dependencies, safety precautions and validation checks needed for recovery.

### Step 9: Test recoverability

Where practical, test the recovery process using a simulator, spare controller or approved test environment. Do not experiment with the only production controller.

## 8. Backup Frequency and Triggers

There is no single frequency suitable for every PLC system. The schedule should reflect the consequences of failure, how often changes occur and how difficult the system is to reconstruct.

| Event | Recommended backup action |
| --- | --- |
| Initial commissioning | Create and verify the approved baseline backup. |
| Approved program change | Save a new revision and update the relevant recovery package. |
| Major configuration change | Back up affected program and configuration items. |
| Firmware change | Preserve the original project and document the new firmware and compatibility state. |
| Controller replacement | Preserve the known-good source and record the restored configuration. |
| Vendor intervention | Obtain and review the updated source project and change records. |
| Periodic maintenance review | Confirm that backups remain accessible, current and recoverable. |
| Before a risky maintenance operation | Create or verify an appropriate recovery point. |
| After successful restoration | Save and document the verified restored state. |

For frequently modified systems, event-based backups after approved changes are especially important. A periodic schedule alone may miss a critical change made the previous day.

## 9. Restore CPU: General Workflow

Restoring a CPU means returning it to the required program and configuration state after failure, replacement, corruption or another recovery event.

The exact procedure varies substantially between controller families. The general workflow is:

Identify the Failed or Target CPU

|

v

Locate the Approved Recovery Package

|

v

Verify Hardware and Firmware Compatibility

|

v

Review Network, I/O and Device Configuration

|

v

Prepare the Replacement or Recovered CPU

|

v

Load the Approved Program and Configuration

|

v

Verify Controller Identity, Mode and Diagnostics

|

v

Verify I/O, Communications and Device Integration

|

v

Perform Approved Functional and Safety Validation

|

v

Document the Restored State

Before starting, establish whether the CPU is truly failed or whether the problem is caused by power, network communication, a faulted module, an incorrect mode, memory configuration or another issue. Replacing a healthy CPU will not fix a failed power supply or network connection.

## 10. Before Replacing a CPU

A controller replacement should begin with diagnosis and compatibility checks, not with the assumption that the CPU is defective.

Check:

CPU power and status indicators.

Power supply and chassis condition, where applicable.

Controller fault and diagnostic information.

Network link and communication status.

I/O module and remote-device status.

Controller operating mode.

Memory card or nonvolatile-storage status.

Firmware and hardware identity.

Whether a known-good backup exists.

Whether the suspected fault could be caused by another component.

For modular systems, verify the chassis, power supply, communication modules and I/O configuration. For compact PLCs, check the integrated I/O, expansion modules and device-specific configuration.

Follow the manufacturer's electrical safety and replacement instructions. Never remove or replace a module under power unless the hardware explicitly supports that operation and the approved procedure permits it.

## 11. CPU Replacement Compatibility

A physically similar CPU is not necessarily a compatible replacement.

| Compatibility factor | Why it matters |
| --- | --- |
| CPU family and model | Determines supported instructions, memory, features and project compatibility. |
| Firmware version | Affects supported functionality and project requirements. |
| Engineering-software version | May be required to open, convert or deploy the project. |
| Memory capacity | The replacement must support the program and required data. |
| Hardware configuration | The project must match the actual chassis, modules or integrated I/O. |
| Network identity | IP address, device name and communication settings may need restoration. |
| Retentive data | Values such as counters, recipes or production states may require separate handling. |
| Safety configuration | Safety-related systems can require additional compatibility checks and validation. |
| Motion or technology configuration | May require specific hardware, firmware, parameters or commissioning. |
| Licensing and dependencies | Some engineering or integrated systems require additional licensed components or external assets. |

A replacement CPU may have a different firmware version or memory configuration. Confirm compatibility before transferring a project.

## 12. Program Restore vs Data Restore

A particularly important distinction is the difference between restoring the program and restoring the data.

### Program restore

Recovers the supported control logic and associated configuration required to execute the intended application.

### Data restore

Recovers application data such as:

Recipe values.

Setpoints.

Retentive counters.

Production parameters.

Calibration values.

Machine-specific configuration.

Certain retained states.

The exact data that can be retained, backed up or restored depends on the PLC and application.

A program can be restored correctly while important production data remains missing or outdated.

For example, a machine may have its original ladder logic but lack approved recipe values or calibration data. The PLC may enter RUN mode, yet the process may not produce acceptable results.

Before restoration, identify which data must be preserved, which should be reinitialized and which must be recovered from an approved source.

## 13. Memory Cards and Nonvolatile Storage

Some PLC families use memory cards or nonvolatile storage to preserve programs, configuration or other supported information.

These mechanisms can simplify recovery, but they must not be treated as universally interchangeable backups.

Important checks include:

Whether the card is compatible with the target CPU.

Whether the stored image matches the intended hardware and firmware.

Whether the stored program is current.

Whether automatic loading is configured and under what conditions.

Whether retained data is included.

Whether the card contains the expected program and configuration.

Whether using it could overwrite a valid controller state.

Whether the manufacturer requires specific procedures for recovery.

Do not insert a card or initiate an automatic restore without understanding what it contains and what the controller is configured to do with it.

## 14. Safety During Restoration

A successful restoration must not create an uncontrolled machine restart or unsafe sequence.

Before restoration:

Establish the machine's safe state.

Follow the approved isolation and lockout/tagout requirements where applicable.

Prevent unexpected motion or energization.

Coordinate with production, maintenance and relevant engineering personnel.

Confirm that the approved project and configuration are being used.

Follow special procedures for safety PLCs, robots, motion systems and hazardous processes.

After restoration:

Confirm the controller's operating mode.

Verify the program and configuration.

Check I/O and communication faults.

Confirm relevant permissives and interlocks.

Test the required sequence under controlled conditions.

Validate safety-related functions according to the approved process.

Confirm that the machine cannot restart unexpectedly.

Obtain the required approval before returning the equipment to production.

Never treat “CPU is in RUN” as proof that the machine is safe or ready for production.

## 15. Vendor-Specific Backup and Restore Awareness

### 15.1 Rockwell Automation: Studio 5000 Logix Designer

Typical considerations for ControlLogix and CompactLogix systems include:

Preserve the native Logix project and associated documentation.

Record the controller catalog number and firmware revision.

Record the chassis and module configuration where applicable.

Preserve relevant communication paths and network settings.

Check controller-resident nonvolatile-memory features if supported.

Understand the implications of uploading, downloading and restoring controller contents.

Use appropriate safety procedures for GuardLogix systems.

A project download and a controller memory restore are not necessarily equivalent operations. The supported behavior depends on the controller family, firmware, memory features and selected operation.

### 15.2 Siemens: STEP 7 and TIA Portal

Typical considerations include:

Preserve the native engineering project.

Record the CPU model and firmware.

Preserve hardware configuration, device names, addressing and relevant network configuration.

Record required engineering-software versions and dependencies.

Understand the specific CPU's memory-card and load-memory behavior.

Use supported backup or retrieval methods for the target CPU.

Perform required safety and functional validation after restoration.

The recovery capabilities of an S7-300, S7-400, S7-1200 and S7-1500 are not identical. Memory architecture, project workflow, firmware and available recovery mechanisms vary.

### 15.3 Mitsubishi: GX Works2 and GX Works3

Typical considerations include:

Preserve the correct native project.

Record the PLC series, CPU model and firmware where applicable.

Back up required programs, parameters and supported device data.

Verify communication settings and hardware configuration.

Follow the controller-specific procedure for reading, writing or restoring stored data.

Validate device behavior and machine sequences after recovery.

The exact backup scope and recovery operations depend on the Mitsubishi PLC family and engineering-software version.

## 16. Common Backup and Restore Failures

| Problem | Possible cause | Recommended action |
| --- | --- | --- |
| Project file is missing | Backup was not stored or was saved to an unknown location. | Search approved engineering storage and recovery locations. |
| Project opens with errors | Wrong software version, corrupted file or missing dependencies. | Preserve the original file and investigate compatibility and integrity. |
| Uploaded program lacks documentation | Original source information was not stored in recoverable controller contents. | Locate the original project, external documentation or revision history. |
| Replacement CPU rejects the project | Model or firmware incompatibility. | Verify hardware compatibility and the supported conversion or deployment procedure. |
| CPU starts but devices do not communicate | Network settings, device configuration, firmware or addressing differs. | Check the configuration and device diagnostics. |
| Program runs but machine behavior differs | Data, parameters, hardware configuration or program revision is incorrect. | Compare the restored state with the approved baseline. |
| Retentive values are missing | Data was not included in the backup or is not retained by the replacement. | Restore approved data separately where supported. |
| Memory card does not restore expected contents | Card mismatch, stale image, incorrect configuration or unsupported operation. | Verify card identity, stored contents and the manufacturer's procedure. |
| Safety-related system does not accept the restored configuration | Safety configuration or validation requirements are unmet. | Follow the specific safety-system recovery and validation process. |
| Restore appears successful but a fault remains | The original fault may involve hardware, network, power or field devices rather than the program. | Diagnose the complete system instead of repeating the same restore. |

## 17. Backup Integrity and Recovery Testing

A backup that has never been checked is an assumption, not a dependable recovery asset.

Useful verification methods include:

Confirming that all expected files are present.

Opening the project in a compatible engineering environment.

Checking the recorded CPU model and firmware.

Reviewing dependencies and hardware configuration.

Confirming that the revision and backup date are documented.

Comparing the backup against the approved project record.

Testing restoration using a simulator or spare controller when practical.

Documenting any components that could not be recovered or validated.

A checksum can help detect accidental file changes, but it does not prove that a PLC project is correct or that the machine can be restored successfully.

Recovery testing should be planned according to the criticality of the machine and the site's requirements.

## 18. Example: Building a Recovery Package for an Automated Line

Suppose a production line contains:

One PLC.

Remote I/O.

Multiple drives.

Robot controllers.

An HMI.

A local SCADA or data-collection computer.

A PLC-only backup may recover the primary logic but still leave the line unable to operate because a robot program, drive parameter set or HMI configuration is missing.

A more complete recovery inventory could look like this:

| System | Required recovery information |
| --- | --- |
| PLC | Native project, controller model, firmware and relevant configuration. |
| Remote I/O | Module configuration, addressing and communication details. |
| Drives | Approved parameter backup, model and firmware information. |
| Robots | Controller-specific programs, configuration and required recovery records. |
| HMI | Native project, runtime dependencies and communication settings. |
| SCADA / industrial PC | Application configuration, required software versions and approved data backup. |
| Network | IP plan, device names and relevant managed-network configuration. |
| Safety system | Approved safety project, configuration and validation records. |
| Engineering environment | Required software versions, libraries, dependencies and licensing information. |

The recovery package should identify the correct revision for each component. Independently restoring the latest available file for every device may produce incompatible versions across the line.

## 19. Example Recovery Record

| Field | Example entry |
| --- | --- |
| Machine / line | FR1010 |
| Controller | Verified CPU model and identity |
| Firmware | Recorded version |
| Engineering software | Vendor software and version |
| Approved project | Revision identifier |
| Backup date | Recorded date and time |
| Backup location | Approved storage location |
| Backup scope | Program, configuration, data and supporting assets included |
| Recovery trigger | CPU failure, corruption or planned replacement |
| Replacement compatibility | Verified model and firmware requirements |
| Restore method | Manufacturer-supported procedure |
| Transfer result | Completed, failed or incomplete |
| Post-restore diagnostics | Recorded controller and module status |
| Functional validation | Test results |
| Safety validation | Required validation record |
| Final approved state | Revision and return-to-service approval |

## 20. Interview Questions and Answers

Q1. What is the difference between a backup and an upload?

An upload retrieves supported controller contents. A backup is a deliberately preserved recovery package that should include the project and any required configuration or supporting information.

Q2. Why is saving the PLC project not always enough?

The project may not contain the necessary data, firmware information, device configuration, external assets or restoration instructions required to recover the complete system.

Q3. What should be checked before restoring a replacement CPU?

Controller compatibility, firmware, project revision, hardware configuration, network settings, required data, safety requirements and the recovery procedure.

Q4. Why can a restored CPU run while the machine still fails?

The program may be running while communication, I/O, device parameters, retained data, sequence conditions or physical equipment remain incorrect.

Q5. What is the difference between program restore and data restore?

Program restore recovers supported logic and configuration. Data restore recovers application values such as recipes, setpoints and other required data.

Q6. Why should a backup be tested?

To establish that it is readable, sufficiently complete and usable under the intended recovery process.

Q7. Can a memory card be treated as a complete backup?

Not automatically. Its contents, compatibility, freshness and supported restore behavior must be verified for the specific controller.

Q8. What should happen after a successful CPU restoration?

Verify controller identity, program revision, diagnostics, communications, I/O behavior, required functional tests and safety validation before returning the machine to service.

Q9. Why should the previous known-good project be preserved?

It provides a reference and potential recovery path if a later change or restoration introduces a problem.

Q10. What is the biggest mistake in PLC recovery planning?

Assuming that the controller program alone is enough to restore the entire machine.

## 21. Practical Exercises

Use a training project, simulator or approved test environment.

1.	Save a PLC project under a clearly identified revision.

2.	Create a separate recovery folder containing the project and a controller-information record.

3.	Document the CPU model, firmware and required engineering-software version.

4.	List which supporting files are needed to restore the machine.

5.	Create a backup inventory for a hypothetical line with PLC, HMI, drives and robots.

6.	Compare two test revisions and record the differences.

7.	Practise opening and verifying a stored project in a compatible environment.

8.	Write a recovery checklist for a replacement CPU.

9.	Identify which application data must be restored separately from the program.

10.	Define the functional and safety checks that would be required before production restart.

Do not practise controller replacement, memory-card restoration or production downloads on live equipment without an approved procedure.

## 22. Final Mental Model

Identify the System

|

v

Establish the Authoritative Project

|

v

Preserve Program, Configuration and Required Data

|

v

Verify Backup Integrity and Compatibility

|

v

Store the Recovery Package Independently

|

v

Diagnose the Failure

|

v

Prepare the Compatible Replacement or CPU

|

v

Restore Using the Supported Procedure

|

v

Validate Program, I/O, Devices and Safety

|

v

Document the Final Approved State

Remember: A PLC backup is not just a file, and CPU restoration is not just a download. Reliable recovery requires the correct project, compatible hardware and firmware, necessary configuration and data, a controlled restoration procedure, and verified machine behavior.

Next study section: 02_PLAN_WISE_2026\02_INDUSTRY3_0\02_Auto_Tech\01_PLC\13_Manufacturer_Awareness\01_Siemens

Next topic: 01_Siemens | Siemens: S7-300/400/1200/1500, STEP 7, TIA Portal