# 02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\01_MPI - MPI

## 1. What is MPI?

MPI stands for Multi Point Interface. It is a Siemens industrial communication interface and protocol historically associated with SIMATIC S7 PLC families, particularly the S7-300 and S7-400, and their programming and operator-interface environments.

MPI was designed to connect compatible Siemens automation devices over a shared communication network. Depending on the hardware and configuration, this could include PLCs, programming devices, operator panels, and other compatible systems.

MPI is particularly relevant when maintaining older Siemens installations, connecting legacy programming software, diagnosing communication faults, or migrating an older control system to a newer architecture.

MPI is not the same as Ethernet, PROFINET, PROFIBUS, or PPI. These technologies can appear in related Siemens systems, but their physical interfaces, protocols, network rules, and configuration requirements differ.

## 2. Where MPI fits in industrial automation

MPI is a communication technology from the Siemens SIMATIC automation ecosystem. It operates in the context of Siemens PLC communication and engineering, rather than being a universal protocol for every manufacturer's controller.

A typical legacy setup may look like this:

STEP 7 Engineering Computer

|

| MPI adapter / compatible interface

|

v

MPI Network

|

+----+----+

|         |

v         v

S7-300     S7-400

PLC        PLC

|

+---- Compatible HMI or other MPI-capable device

The diagram is conceptual. The actual devices, connection topology, supported participants, and communication services depend on the installed hardware and firmware.

### Common applications

Connecting a programming computer to a legacy Siemens PLC.

Uploading or downloading a project with compatible Siemens engineering software.

Monitoring PLC status and diagnosing faults.

Connecting supported HMI or operator devices.

Exchanging data between compatible automation participants.

Supporting maintenance during legacy-system operation or migration.

Not every device connected to an MPI network can perform every function. A programming device, HMI, and PLC may use different communication services even when they share the same network.

## 3. MPI hardware and physical connection

MPI is associated with Siemens' legacy serial-style automation interfaces. Many installations use a 9-pin D-sub connector and RS-485-based electrical signaling, but the precise interface depends on the controller and communication hardware.

The connector alone does not establish that a port supports MPI. Similar-looking connectors can be used for different interfaces and protocols.

### 3.1 Typical components

| Component | Function |
| --- | --- |
| MPI-capable PLC port | Connects the PLC to the MPI network |
| Programming device | Runs compatible engineering software and communicates with the PLC |
| PC/MPI adapter | Converts the PC-side interface to the required Siemens communication interface |
| MPI cable | Carries the communication signals between compatible devices |
| HMI or operator panel | Exchanges supported operator or data communication with the PLC |
| Bus termination | Supports electrical signal integrity where required by the network design |
| Network configuration | Defines parameters such as participant addresses and communication speed |

The exact adapter, cable, pinout, and termination requirements must be confirmed from the specific Siemens hardware manual. A generic RS-232 or RS-485 converter is not automatically an MPI adapter.

### 3.2 MPI and RS-485

RS-485 describes electrical signaling characteristics. MPI describes a Siemens communication system and its protocol behavior.

These are different layers of the system:

Electrical interface: Defines how signals are electrically represented.

Physical network: Defines how devices and wiring are connected.

Communication protocol: Defines how devices exchange and interpret messages.

Engineering application: Defines functions such as PLC programming, diagnostics, and data access.

A generic RS-485 converter may provide compatible electrical signaling but still lack the protocol handling, timing, or driver support needed for MPI communication.

This is why choosing an adapter based only on the connector or the words "serial converter" is a reliable way to acquire a device that does absolutely nothing useful.

## 4. MPI addressing

MPI uses MPI station addresses, not IP addresses. Each participant on the same MPI subnet must have a unique address.

An MPI address identifies a device or communication participant within the MPI network. It is not an Ethernet address and cannot be used as an IP address.

### 4.1 Addressing example

| Device | Example MPI address | Purpose |
| --- | --- | --- |
| Programming device (PG/PC) | 0 | Commonly reserved for engineering access |
| PLC 1 | 2 | First PLC participant |
| PLC 2 | 3 | Second PLC participant |
| HMI | 4 | Operator interface |
| Additional compatible station | 5 | Another configured participant |

These are illustrative addresses, not a universal configuration. Follow the existing project's network configuration and the specific device manuals.

### 4.2 Addressing rules

Every participant in the same MPI subnet must have a unique address.

Address assignments must match the actual physical network and configured devices.

The programming device must use a compatible interface configuration and address.

Some CPUs and communication modules have default addresses, but defaults must not be assumed to be unique across the entire network.

Communication parameters should be checked before downloading a changed network configuration.

A duplicate address can cause communication instability or prevent devices from communicating correctly. When diagnosing a legacy system, record the existing addresses before changing anything.

## 5. MPI baud rate and network parameters

The baud rate defines the signaling speed used by the communication interface. It must be compatible with the connected devices and the network configuration.

Common MPI speeds include:

19.2 kbit/s.

187.5 kbit/s.

Higher rates supported by particular CPU and interface combinations, potentially up to 12 Mbit/s on supported hardware.

The actual supported range depends on the CPU, interface, firmware, and connected equipment. A default value commonly found on legacy S7-300/S7-400 systems is 187.5 kbit/s.

### 5.1 Parameters to verify

| Parameter | What to check |
| --- | --- |
| MPI address | Unique address for each participant |
| Baud rate | Matching supported network speed |
| Highest station address | Consistent with the configured network |
| Network topology | Correct wiring and compatible bus components |
| Termination | Correct termination at the appropriate bus ends |
| PG/PC interface | Correct adapter and communication driver selected |
| CPU interface mode | Confirm MPI mode rather than PROFIBUS DP mode where the port supports both |
| Hardware compatibility | CPU, adapter, cable, and software support |

Important: Some Siemens interfaces can be configured for either MPI or PROFIBUS DP operation. A connector labeled MPI/DP does not necessarily operate in MPI mode at all times. Verify the configured interface mode in the project and the actual CPU.

## 6. MPI communication architecture

MPI is a multi-participant network. Compatible devices communicate over a shared network, with each participant assigned an address and communication parameters.

A typical engineering connection works as follows:

Engineering software

↓

PC communication driver

↓

Compatible PC/MPI adapter

↓

MPI electrical interface

↓

MPI network

↓

Target PLC address

↓

PLC communication service

Each layer must work correctly.

The engineering software must support the target PLC.

The correct PC communication driver must be selected.

The adapter must support the required interface and speed.

The physical connection must be correct.

The target address and bus parameters must match.

The PLC must support the requested service.

A fault at any layer can prevent the programming device from going online.

## 7. Connecting a PC to an MPI PLC

For legacy Siemens systems, the engineering software commonly used is STEP 7 Classic with SIMATIC Manager. The precise version and supported operating system depend on the installed CPU and engineering environment.

### 7.1 Required items

Before connecting, identify:

The exact PLC model and CPU order number.

Whether the relevant port is configured for MPI.

The required PC/MPI adapter or communication processor.

The cable and connector requirements.

The installed STEP 7 version and required drivers.

The PLC's MPI address and network parameters.

The approved backup and recovery procedure.

### 7.2 Typical connection procedure

1.	Identify the PLC and verify that its communication port supports MPI.

2.	Inspect the existing project and record the MPI address, baud rate, and interface mode where available.

3.	Install the supported adapter and its driver.

4.	Connect the adapter to the PC and the appropriate PLC interface using the correct cable.

5.	Open the STEP 7 communication configuration, commonly through Set PG/PC Interface in STEP 7 Classic.

6.	Select the correct communication interface, such as the applicable PC Adapter MPI driver.

7.	Configure or verify the local adapter parameters and MPI settings.

8.	Use the engineering software's accessible-node or online diagnostic function, where supported, to identify the target.

9.	Verify the PLC identity before attempting any write or download operation.

10.	Upload or download only under the site's approved procedure.

Menu names and available options vary by STEP 7 release, adapter, and installed drivers.

### 7.3 Uploading versus downloading

These operations are not interchangeable.

| Operation | Meaning | Main risk |
| --- | --- | --- |
| Upload from PLC | Retrieve supported program or configuration information from the controller | The retrieved data may not include every original project artifact or comment |
| Download to PLC | Transfer program or configuration data from the engineering computer to the controller | Can change machine behavior or interrupt production |
| Online monitoring | Observe live program states and values | Incorrect interpretation may lead to faulty diagnosis |
| Online modification | Change selected program or data elements while connected | May alter live machine operation |
| Hardware configuration download | Transfer hardware or communication configuration | May change interfaces, addresses, or communication behavior |

Before an upload, determine whether the goal is to retrieve the current executable, recover an engineering project, or create a full backup. These are different tasks.

Before a download, confirm the correct PLC, CPU operating state, project version, machine conditions, and authorization. A communication test should never become an accidental production change.

## 8. MPI compared with related Siemens communication technologies

| Technology | Primary distinction | Typical context |
| --- | --- | --- |
| MPI | Siemens multi-point communication interface and protocol | Legacy S7-300/S7-400 engineering and communication |
| PPI | Point-to-Point Interface associated with S7-200 systems | Legacy S7-200 programming and communication |
| PROFIBUS | Industrial fieldbus technology with defined network and device communication mechanisms | PLCs, remote I/O, drives, and field devices |
| Industrial Ethernet | Ethernet-based industrial communication infrastructure and protocols | Modernized PLC, HMI, SCADA, and device networks |
| PROFINET | Industrial Ethernet communication system | Controller-to-device communication, distributed I/O, and automation networks |

### 8.1 MPI versus PPI

MPI is primarily associated with compatible S7-300/S7-400 systems, while PPI is associated with S7-200 systems. Both are Siemens technologies, but they are not interchangeable.

An adapter may support multiple modes, but that does not mean every mode supports every PLC. For example, a compatible adapter might offer separate MPI and PPI driver selections. The correct choice depends on the target CPU, adapter model, and software.

### 8.2 MPI versus PROFIBUS

MPI and PROFIBUS can share aspects of physical wiring and bus technology in certain installations, but they are distinct communication systems.

MPI uses Siemens-specific communication mechanisms and MPI addressing.

PROFIBUS supports defined fieldbus communication arrangements, including DP for distributed peripherals.

An MPI/DP interface may be configured for one mode or another, depending on the hardware.

Do not assume that a PROFIBUS configuration can be used unchanged on an MPI network simply because the connector and wiring look similar.

### 8.3 MPI versus PROFINET

MPI is a legacy serial-style interface. PROFINET uses industrial Ethernet infrastructure and IP-based network configuration for many functions.

Typical differences include:

MPI uses MPI station addresses and bus parameters.

PROFINET uses Ethernet networking, device naming, and IP configuration as appropriate to the application.

MPI uses compatible MPI adapters and drivers.

PROFINET uses suitable Ethernet interfaces and compatible engineering drivers.

Migration from MPI to PROFINET may require hardware, software, communication, and network-architecture changes.

A migration should account for the actual communication services in use, not just the physical cable.

## 9. MPI fault diagnosis

When a programming computer cannot find a PLC, isolate the problem rather than replacing parts at random.

### 9.1 Common symptoms and causes

| Symptom | Possible cause | Diagnostic action |
| --- | --- | --- |
| No PLC appears in accessible nodes | Wrong driver, adapter issue, disconnected cable, incorrect interface mode | Verify the adapter, driver, cable, and PLC port |
| PLC appears intermittently | Loose connector, electrical interference, termination issue, multiple communication participants | Inspect wiring and bus configuration |
| PLC is visible but cannot go online | Wrong target address, unsupported CPU, software compatibility issue | Verify the CPU identity, address, and engineering software |
| Communication works with one PC but not another | Driver or adapter configuration differs | Compare PG/PC interface settings and driver installation |
| Communication fails after a CPU or interface change | Address, baud rate, or interface mode changed | Compare current settings with the approved project |
| Multiple PLCs cause unstable communication | Duplicate MPI addresses or incorrect network parameters | Verify unique addresses and consistent bus settings |
| Adapter is detected by Windows but PLC is unavailable | USB driver is present, but MPI-side communication is failing | Check the MPI connection, driver selection, and network parameters |
| Communication degrades after wiring work | Incorrect topology, termination, damaged cable, or poor connection | Inspect the physical bus and applicable installation requirements |
| A new adapter does not work | Adapter lacks MPI support or requires a different driver | Confirm exact adapter compatibility and supported operating mode |

### 9.2 Diagnostic order

Use this sequence:

1.	Identify the hardware. Read the CPU model and the interface labels. Determine whether the interface is MPI, MPI/DP, or another interface.

2.	Check physical connection. Inspect the adapter, cable, connector, and power or status indicators.

3.	Check the PC driver. Confirm the operating system recognizes the adapter and the required communication driver is installed.

4.	Check PG/PC interface selection. Ensure STEP 7 uses the adapter and protocol intended for the target.

5.	Check MPI parameters. Verify address, baud rate, and compatible network configuration.

6.	Check station addresses. Look for duplicate addresses and incorrect target selection.

7.	Check the CPU and software combination. Confirm that the engineering software supports the installed CPU and firmware.

8.	Inspect the network. Investigate wiring, termination, interference, and connected devices if communication remains unstable.

9.	Compare with a known-good configuration. Use documented settings from a verified machine or approved backup.

10.	Record the outcome. Document the root cause and preserve the working configuration.

Do not change a live network's baud rate or participant addresses casually. Such changes can disconnect other devices or interrupt communication with the PLC.

## 10. Maintenance, backup, and migration considerations

MPI is especially important when maintaining older equipment whose original engineering tools or adapters are no longer readily available.

### 10.1 Legacy-system records

For each MPI-connected machine, maintain a record of:

PLC model and order number.

CPU firmware and installed communication modules.

Interface type and operating mode.

MPI address and baud rate.

Connected HMI and programming devices.

Adapter model, driver, and compatible engineering software.

Verified project backup and date of last successful upload.

Known-good cable and adapter part numbers.

Known faults, workarounds, and recovery procedures.

Migration constraints and available replacement hardware.

### 10.2 Backup discipline

A backup plan should distinguish the PLC's current executable and configuration from the original editable engineering project.

Where possible, retain:

The original engineering project with symbols, comments, and documentation.

A verified upload from the running PLC.

Hardware configuration and communication settings.

Compatible software installers, drivers, and licensing information.

A record of the CPU's actual state and version.

A documented restoration and validation procedure.

A successful upload does not guarantee that all original source-level information has been recovered. If the original project is missing, preserve the uploaded data and investigate what can be reconstructed before making changes.

### 10.3 Migration planning

When replacing an MPI-connected PLC or network, assess:

Whether the replacement controller supports the existing interface.

Whether the HMI and other participants can still communicate.

Whether the existing protocol services can be reproduced.

Whether a gateway or communication processor is needed.

Whether wiring, power, and network components must change.

Whether the application should migrate to PROFIBUS or PROFINET.

Whether the old engineering software and adapter must be retained during the transition.

How to test the migrated system before returning the machine to production.

The objective is not simply to replace a port. It is to preserve the required machine functions and communication relationships.

## 11. Safety and operational precautions

Obtain authorization before connecting engineering equipment to a production PLC.

Confirm the correct controller before uploading, modifying, or downloading.

Preserve the original project and record the current configuration before changes.

Avoid changing interface modes, baud rates, or addresses during production without an approved plan.

Consider the effect of connecting or disconnecting devices on legacy networks.

Use the hardware-specific manual for wiring, termination, and adapter requirements.

Follow the site's lockout, machine-state, and change-control requirements when work could affect hazardous motion or process behavior.

Validate the machine's operation and communication after maintenance.

Communication availability does not establish functional safety. MPI itself should not be treated as a safety-rated control channel unless the complete, specific architecture is explicitly designed and certified for that purpose.

## 12. Interview questions and answers

Q1. What does MPI stand for?

MPI stands for Multi Point Interface, a Siemens communication interface associated with legacy SIMATIC automation systems.

Q2. Which PLC families are commonly associated with MPI?

MPI is commonly associated with SIMATIC S7-300 and S7-400 systems, although exact support depends on the CPU and interface hardware.

Q3. Does MPI use IP addresses?

No. MPI participants use MPI station addresses. IP addressing applies to IP-based networks such as Industrial Ethernet and PROFINET-related networking functions.

Q4. What is the purpose of an MPI adapter?

It provides a compatible communication interface between a programming computer and an MPI-capable automation system. It may also require an appropriate driver and engineering software configuration.

Q5. Why is a generic RS-485 converter not necessarily suitable for MPI?

RS-485 defines electrical signaling, not the complete MPI protocol. A generic converter may lack the required communication handling, timing, and driver support.

Q6. What is the purpose of a unique MPI address?

It distinguishes each participant within the MPI subnet so communication can be directed to the intended device without address conflicts.

Q7. What should be checked when STEP 7 cannot find an MPI PLC?

Check the physical connection, adapter compatibility, driver installation, PG/PC interface selection, MPI address, baud rate, interface mode, and CPU/software compatibility.

Q8. What is the difference between MPI and PROFIBUS?

MPI is a Siemens-specific multi-point communication system. PROFIBUS is an industrial fieldbus technology with defined communication arrangements such as PROFIBUS DP. Similar physical components do not make the protocols interchangeable.

Q9. What is the difference between MPI and PROFINET?

MPI is a legacy serial-style interface using MPI station addressing. PROFINET uses industrial Ethernet technology and corresponding network configuration.

Q10. Why should the MPI configuration be documented before maintenance?

Because changing the address, baud rate, or interface mode can disrupt existing communication. A verified record helps restore the network and reduces downtime.

Q11. Does uploading a PLC program always recover the original engineering project?

No. The uploaded data may lack original comments, symbols, source organization, and other project artifacts. Preserve both the original editable project and a verified PLC upload when possible.

Q12. What is the main concern when migrating an MPI system?

Ensuring that the PLC, HMI, engineering tools, communication services, wiring, and machine functions remain compatible or are properly replaced and validated.

## 13. Practical exercises

1.	Identify the interface: Inspect an available legacy Siemens PLC's model and interface labels. Determine whether the port supports MPI, PROFIBUS DP, or a configurable MPI/DP mode.

2.	Build an MPI address table: For a documented lab network, record each participant's address, device type, and role. Check that addresses are unique.

3.	Inspect the engineering setup: Open the PG/PC interface settings on an authorized engineering computer and identify the selected adapter and driver.

4.	Create a fault tree: Write a troubleshooting sequence for a PLC that does not appear in accessible nodes, separating PC-driver faults, adapter faults, physical-layer faults, and configuration faults.

5.	Prepare a backup record: List the CPU identity, project version, communication settings, adapter model, and restoration requirements for a legacy machine.

6.	Compare migration options: For a hypothetical MPI-connected PLC, document the hardware and software changes required to move to an Ethernet-based architecture.

## 14. Final mental model

MPI: Siemens multi-point communication technology used in compatible legacy automation systems.

MPI address: Identifies a participant within the MPI subnet.

Baud rate: Must be compatible with the CPU, adapter, and network configuration.

Adapter: Bridges the engineering computer to the required MPI interface.

PG/PC interface: Selects the communication driver and connection used by engineering software.

Physical layer: Cable, connector, wiring, and termination must be correct.

Protocol layer: The device and software must support the intended communication service.

Maintenance discipline: Record settings, preserve backups, verify the target, and make controlled changes.

Migration: Preserve required functions and compatibility rather than assuming a new interface is a direct replacement.

## NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\02_PPI - PPI