# 02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\02_PPI - PPI

## 1. What is PPI?

PPI stands for Point-to-Point Interface. It is a Siemens communication protocol associated primarily with the SIMATIC S7-200 PLC family. It was designed to support communication between S7-200 controllers and compatible devices such as programming computers and operator panels.

PPI is important when maintaining legacy Siemens equipment, connecting STEP 7-Micro/WIN engineering software, diagnosing PLC communication faults, or recovering an older machine's control program.

Despite the name, PPI networks can support multiple participants in supported configurations. The name should not be interpreted as a guarantee that only two devices can exist on the network.

PPI is distinct from MPI, PROFIBUS, and PROFINET. All belong to the wider industrial automation communication landscape, but they differ in protocol behavior, device compatibility, addressing, and configuration.

## 2. Where PPI fits in industrial automation

PPI is commonly associated with the Siemens S7-200 PLC family. It appears in legacy machines where the controller handles machine sequencing, digital and analog I/O, basic process control, and communication with an HMI or programming device.

Typical applications include:

Connecting a programming computer to an S7-200 PLC.

Uploading or downloading a PLC program using compatible engineering software.

Monitoring program execution and PLC data.

Connecting a supported HMI to an S7-200.

Communicating with compatible Siemens devices through the configured PPI network.

Maintaining older machines that have not yet migrated to newer controller platforms.

A typical arrangement looks like this:

Engineering PC

STEP 7-Micro/WIN

|

| Compatible PPI adapter

|

v

PPI network

|

+--+----------------+

|                   |

v                   v

S7-200 PLC          Compatible HMI

|

v

Machine I/O, sensors, actuators

The actual topology depends on the PLC port, adapter, cable, HMI, and supported network configuration.

## 3. PPI hardware and physical interface

PPI is commonly associated with the serial communication interface on S7-200 CPUs. Many installations use an RS-485-based physical interface, often through a 9-pin D-sub connector or a compatible Siemens connector arrangement.

However, a connector's appearance alone does not establish its protocol. Always identify the exact CPU and port before connecting an adapter.

### 3.1 Main components

| Component | Function |
| --- | --- |
| S7-200 CPU | Executes the PLC program and provides the supported communication interface |
| PPI-capable port | Connects the controller to the PPI network |
| Programming computer | Runs compatible engineering software |
| PPI adapter | Provides the required interface between the PC and PPI network |
| Communication cable | Connects the adapter to the PLC or network |
| HMI | Exchanges supported operator commands and process data |
| Network configuration | Defines station addresses and communication parameters |

A generic USB-to-serial converter is not necessarily a PPI adapter. A generic RS-485 converter may support the electrical signaling but still lack the protocol compatibility, timing, or driver support required by the engineering software.

### 3.2 PPI and RS-485

These terms refer to different aspects of communication.

RS-485: Defines electrical signaling characteristics for a balanced serial interface.

PPI: Defines Siemens communication behavior used by compatible devices.

PPI adapter: Provides the required PC-to-network interface and protocol support.

STEP 7-Micro/WIN: Provides the engineering functions used to program and diagnose supported S7-200 PLCs.

Correct electrical signaling alone does not guarantee successful communication. The protocol, adapter, driver, and software must also be compatible.

## 4. PPI addressing

PPI uses station addresses to identify communication participants. These are not IP addresses.

The engineering computer, PLC, and compatible HMI must use compatible addressing and communication settings. Address ranges and defaults depend on the specific S7-200 configuration and connected equipment.

### 4.1 Example station-address plan

| Device | Example station address | Purpose |
| --- | --- | --- |
| Engineering PC | 0 | Programming and diagnostics |
| S7-200 PLC | 2 | Machine controller |
| HMI | 3 | Operator interface |
| Additional compatible device | 4 | Additional network participant |

These values are illustrative, not mandatory defaults. Use the addresses configured in the actual project and devices.

### 4.2 Addressing rules

Each participant on the same logical network should have a unique address.

The programming software must target the correct PLC address.

The HMI's configured PLC address must match the intended controller.

Changes must be coordinated with other network participants.

A device's physical connection does not automatically assign it the correct logical address.

If two devices use the same address, communication may become unreliable or fail, depending on the devices and network behavior.

## 5. PPI communication speed and parameters

PPI communication speed must be supported by the CPU, adapter, and engineering software. Different S7-200 models, firmware versions, and adapter types can support different combinations.

Commonly encountered PPI speeds include 9.6 kbit/s and 19.2 kbit/s. Some S7-200 configurations and compatible interfaces support 187.5 kbit/s. Do not assume every CPU or adapter supports every speed.

### Parameters to verify

| Parameter | Purpose |
| --- | --- |
| Station address | Identifies the local or target participant |
| Baud rate | Defines the communication signaling speed |
| Target PLC address | Identifies the controller being accessed |
| Adapter mode | Ensures the adapter operates in a compatible PPI mode |
| Communication driver | Allows the engineering software to use the adapter |
| CPU model | Establishes protocol and software compatibility |
| Port configuration | Confirms that the selected physical port supports the required communication |
| Network wiring | Ensures correct connections and electrical integrity |

A mismatch between the PC's communication settings and the PLC's configuration can prevent communication even when the cable and adapter are functional.

## 6. Connecting a PC to an S7-200 PLC

The traditional engineering environment for S7-200 controllers is STEP 7-Micro/WIN. It is distinct from STEP 7 Classic, which is commonly associated with S7-300 and S7-400 engineering.

The exact software version, operating-system support, adapter model, and driver requirements depend on the installed S7-200 CPU and engineering setup.

### 6.1 Before connecting

Identify:

The exact S7-200 CPU model.

The communication port and supported protocol.

The adapter model and required driver.

The installed STEP 7-Micro/WIN version.

The PLC station address and communication speed.

The existing program backup and machine operating state.

### 6.2 Typical connection procedure

1.	Identify the PLC model and confirm that the selected port supports PPI.

2.	Inspect the existing project or machine documentation for communication settings.

3.	Install a compatible PPI adapter and its supported driver.

4.	Connect the PC, adapter, and PLC using the correct cable.

5.	Open the communication or interface configuration in STEP 7-Micro/WIN.

6.	Select the appropriate adapter or communication interface.

7.	Configure the communication parameters required by the PLC.

8.	Search for or select the intended PLC using the available communication functions.

9.	Verify the PLC identity before accessing or modifying its program.

10.	Perform uploads, downloads, or online modifications only under the approved maintenance procedure.

Software menus and interface names vary by version and adapter. Use the manual for the exact equipment rather than assuming every installation follows the same menu sequence.

## 7. Upload, download, and online monitoring

These operations have different purposes and risks.

| Operation | Purpose | Main consideration |
| --- | --- | --- |
| Upload from PLC | Retrieve supported program or data from the controller | May not recover all original engineering documentation |
| Download to PLC | Transfer a program or supported configuration to the controller | Can change machine behavior and may interrupt production |
| Online monitoring | Observe live program states or data | Values must be interpreted in the context of the running sequence |
| Online modification | Change supported program elements or data while connected | Can directly affect machine operation |
| Program comparison | Compare available program representations | Differences may reflect source, configuration, or project-version changes |

Before downloading, confirm the correct PLC, the intended program version, the machine state, and the potential effects on outputs and sequence execution.

A successful upload is not necessarily a complete restoration of the original engineering project. Preserve the original project, symbols, comments, and documentation whenever available.

## 8. PPI network behavior

PPI is a protocol used by compatible Siemens devices to exchange information over a supported serial communication interface. Depending on the configuration, the communication may involve programming requests, operator data exchange, and communication between supported participants.

The actual exchange depends on the protocol implementation and device capabilities.

Engineering application

↓

PPI communication driver

↓

Compatible adapter

↓

Serial physical interface

↓

PPI protocol exchange

↓

Target S7-200 PLC

↓

Program, data, or diagnostic response

A successful connection depends on every layer functioning correctly.

The engineering software must support the target CPU.

The PC driver must recognize and operate the adapter.

The adapter must support PPI.

The physical cable and interface must be correct.

The station address and communication speed must match.

The PLC must be available and support the requested operation.

## 9. PPI compared with MPI, PROFIBUS, and PROFINET

| Feature | PPI | MPI | PROFIBUS | PROFINET |
| --- | --- | --- | --- | --- |
| Primary association | Siemens S7-200 | Siemens S7-300/S7-400 legacy systems | Industrial fieldbus systems | Industrial Ethernet systems |
| Addressing | PPI station address | MPI station address | PROFIBUS station address | Ethernet and device configuration, including IP where applicable |
| Typical engineering tool | STEP 7-Micro/WIN | STEP 7 Classic | Depends on the PLC and fieldbus configuration | TIA Portal or compatible engineering environment |
| Physical interface | Commonly serial and RS-485-based | Commonly serial and RS-485-based | Commonly RS-485 for PROFIBUS DP | Ethernet |
| Main use | S7-200 programming and supported device communication | Legacy Siemens engineering and communication | Controller, remote I/O, drive, and field-device communication | Ethernet-based controller and device communication |
| Interchangeability | Not interchangeable by default | Not interchangeable by default | Requires compatible protocol support | Requires compatible Ethernet hardware and configuration |

### 9.1 PPI versus MPI

Both are Siemens communication technologies, but they serve different controller families and engineering environments.

PPI is primarily associated with the S7-200.

MPI is commonly associated with the S7-300 and S7-400.

Their adapters, drivers, addresses, and communication configurations are not automatically interchangeable.

A multi-protocol adapter may support both PPI and MPI modes, but the required mode must be selected and supported by the target hardware.

### 9.2 PPI versus PROFIBUS

PPI and PROFIBUS can involve similar electrical interface technologies, but they are not the same protocol.

A device using an RS-485 physical interface does not automatically support PROFIBUS DP. Likewise, a PROFIBUS adapter is not automatically a valid PPI adapter.

Confirm the protocol supported by the device, not merely the connector type.

### 9.3 PPI versus PROFINET

PPI is associated with legacy serial communication, while PROFINET uses industrial Ethernet.

Moving from PPI to PROFINET generally involves more than changing a cable. It may require a different PLC, compatible communication hardware, program modifications, HMI changes, and network configuration.

## 10. PPI troubleshooting

### 10.1 Common symptoms

| Symptom | Possible cause | Diagnostic action |
| --- | --- | --- |
| PLC not detected | Wrong driver, adapter, cable, or target address | Verify the physical connection and software configuration |
| Adapter not recognized | Missing driver, incompatible hardware, USB issue | Check device recognition and supported driver requirements |
| PLC detected but online access fails | Incorrect target selection, CPU incompatibility, software issue | Verify the CPU identity and engineering environment |
| Intermittent communication | Loose connection, electrical interference, incompatible settings | Inspect wiring and communication parameters |
| Communication fails after replacing a PC | Different driver or adapter configuration | Compare the old and new engineering setups |
| Communication fails after CPU replacement | Different model, firmware, port behavior, or configuration | Verify CPU and software compatibility |
| HMI cannot communicate with PLC | Incorrect PLC address, baud rate, or HMI driver configuration | Compare the HMI configuration with the PLC and network |
| Download fails | Communication instability, software compatibility, access or operating-state issue | Confirm the target, connection stability, and download requirements |
| PLC works with one adapter but not another | Adapter incompatibility or incorrect operating mode | Confirm the exact adapter model and supported protocol |
| Communication fails after wiring work | Damaged cable, incorrect connections, or electrical fault | Inspect the physical interface and wiring against the manual |

### 10.2 Recommended diagnostic sequence

1.	Identify the CPU. Confirm the exact S7-200 model and available communication ports.

2.	Verify the adapter. Confirm that it explicitly supports the required PPI configuration.

3.	Check the PC driver. Make sure the operating system recognizes the adapter and the required driver is installed.

4.	Inspect the cable. Check the connector, wiring, and physical condition.

5.	Verify software settings. Confirm that STEP 7-Micro/WIN is configured to use the correct interface.

6.	Check station addresses. Ensure the PC and target PLC use the expected addresses.

7.	Verify baud rate. Match the communication speed to the actual supported configuration.

8.	Check compatibility. Confirm that the CPU, adapter, driver, and engineering software are compatible.

9.	Test without changing the running program. Establish reliable communication and identify the PLC before attempting program changes.

10.	Document the result. Record the fault, evidence, corrective action, and verified settings.

Do not repeatedly change communication parameters without recording the original values. On legacy equipment, the working configuration may be difficult to reconstruct.

## 11. Maintenance and legacy-system management

For an S7-200 machine, retain the following information in the machine's maintenance records:

CPU model and order number.

Firmware or hardware revision where available.

PPI address and baud rate.

Adapter model and driver version.

STEP 7-Micro/WIN version.

HMI model and communication settings.

Verified PLC program backup.

Original editable project and related documentation.

Known-good communication cable and adapter details.

Known faults, troubleshooting steps, and restoration procedure.

### Backup discipline

Maintain a clear distinction between the running controller program and the complete editable engineering project.

Where possible, preserve both:

The original engineering project, including comments and symbols.

A verified upload from the running PLC.

Configuration records and software versions.

A documented restoration procedure.

A known-good communication setup.

If the original project is missing, preserve the available upload and establish which documentation and project details can be recovered before modifying the controller.

### Migration considerations

When modernizing an S7-200 installation, assess:

Whether the replacement PLC supports the existing HMI.

Whether the original PPI communication services must be retained temporarily.

Whether a gateway or protocol conversion is appropriate.

Whether the machine should migrate to an Ethernet-based architecture.

Whether existing software, drivers, and adapters must be retained for recovery.

How program behavior and machine interfaces will be validated after migration.

The aim is to preserve machine functionality and maintainability, not simply to replace obsolete hardware.

## 12. Safety and operational precautions

Confirm the target PLC before making changes.

Preserve a verified backup before downloading a modified program.

Follow the plant's change-control and machine-state requirements.

Avoid changing communication settings during production without an approved plan.

Use only compatible adapters and documented wiring arrangements.

Consider the consequences of interrupting communication with the HMI or other participants.

Verify machine operation after any program or communication change.

PPI communication is not, by itself, a functional-safety mechanism. A normal programming or data connection must not be assumed to provide safety-rated behavior.

## 13. Interview questions and answers

Q1. What does PPI stand for?

PPI stands for Point-to-Point Interface, a Siemens communication protocol primarily associated with the S7-200 PLC family.

Q2. Which PLC family commonly uses PPI?

The Siemens SIMATIC S7-200 family.

Q3. Which engineering software is traditionally used for S7-200 programming?

STEP 7-Micro/WIN, with the exact version depending on the PLC and installation.

Q4. Does PPI use IP addresses?

No. PPI uses station addresses within its communication network. IP addressing belongs to IP-based networking.

Q5. Is a USB-to-serial converter sufficient for PPI?

Not necessarily. The adapter must support the required PPI communication mode, with compatible drivers and engineering software.

Q6. What is the relationship between PPI and RS-485?

RS-485 describes electrical signaling characteristics commonly used by PPI interfaces. PPI defines the communication protocol, so electrical compatibility alone is insufficient.

Q7. How would you troubleshoot an S7-200 PLC that is not detected by Micro/WIN?

Check the CPU and port, adapter compatibility, driver, cable, communication settings, station address, and engineering software compatibility.

Q8. Can an MPI adapter be used for PPI?

Some adapters support both protocols, but the exact model, driver, operating mode, and target CPU must be compatible.

Q9. Is PPI the same as PROFIBUS?

No. They are different protocols, even though both may use serial physical interfaces in certain implementations.

Q10. Why is a verified upload useful?

It provides a record of the available program from the running PLC and can support recovery when the original project is missing. It may not contain all original source-level documentation.

Q11. What should be recorded before changing PPI settings?

The PLC identity, station addresses, baud rate, adapter and driver, software version, HMI settings, and current backup status.

Q12. What is the main concern when migrating an S7-200 machine?

Maintaining compatibility and preserving the required control, HMI, and communication functions while validating the replacement system.

## 14. Practical exercises

1.	Identify an available S7-200 CPU and document its model, communication port, and supported protocol.

2.	Prepare a PPI station-address table for a documented lab setup, including the PLC, programming computer, and HMI.

3.	Inspect an authorized engineering computer and record its adapter model, driver, and STEP 7-Micro/WIN version.

4.	Create a troubleshooting checklist for the symptom "PLC not detected."

5.	Prepare a backup register distinguishing the original editable project from a PLC upload.

6.	Compare PPI and MPI requirements for a legacy machine and explain why a compatible multi-protocol adapter must still be configured correctly.

## 15. Final mental model

PPI: Siemens communication protocol associated primarily with S7-200 PLCs.

Station address: Identifies a participant in the PPI network.

Baud rate: Must match a supported communication configuration.

Adapter: Provides a compatible PC-to-PPI interface.

Engineering software: Must support the target PLC and adapter.

Physical connection: Correct cable and port are necessary but not sufficient.

Troubleshooting: Isolate hardware, driver, configuration, and protocol problems systematically.

Maintenance: Preserve the project, verified upload, settings, and recovery procedure.

Migration: Validate machine and communication functionality before returning the system to production.

## NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\03_PROFIBUS\01_Basics - Basics: RS-485 fieldbus, master/slave