# 02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\11_EtherNet_IP\02_Setup - Setup: IP, EDS file, RPI

## 1. Purpose of EtherNet/IP Setup

Setting up EtherNet/IP means configuring the network addressing, identifying devices, defining communication connections, and verifying that industrial data transfers correctly between controllers and devices.

A working Ethernet cable is only the beginning. A device can have a link light and respond to ping while its PLC I/O connection remains faulted. Each configuration layer must be verified independently.

A typical commissioning sequence is:

Identify hardware and firmware

↓

Plan IP addresses and subnet

↓

Configure device network settings

↓

Verify Ethernet and IP connectivity

↓

Install or verify EDS/device description

↓

Configure controller and I/O connection

↓

Set and validate RPI

↓

Test data, faults, and machine operation

↓

Save backups and commissioning records

This topic focuses on three core areas: IP configuration, EDS files, and Requested Packet Interval (RPI), along with the related controller and network settings needed to make them work together.

## 2. Before Configuration: Identify the Devices

Before assigning addresses or editing a controller project, collect the identity and compatibility information for every device involved.

Record:

Manufacturer and exact catalog number.

Hardware revision, where relevant.

Firmware revision.

Ethernet port count and supported network features.

Current IP address and subnet mask.

Default gateway, if required.

Device name or identity, if used by the device.

Supported EtherNet/IP connection types.

Required controller and engineering software versions.

Current project and device configuration backups.

For Rockwell systems, relevant components may include ControlLogix or CompactLogix controllers, EtherNet/IP communication modules, POINT I/O or other remote I/O adapters, drives, robots, and HMIs.

Do not assume every device supports the same configuration method. Some devices use rotary switches, some use a BOOTP/DHCP process, and others provide a web interface or vendor configuration utility.

## 3. IP Address Planning

### 3.1 IP address

An IPv4 address identifies a device interface on an IP network.

Example addressing plan for an isolated machine network:

| Device | Example IP address | Purpose |
| --- | --- | --- |
| PLC | 192.168.10.10 | Machine control |
| Remote I/O adapter | 192.168.10.20 | Distributed I/O |
| VFD | 192.168.10.30 | Drive communication |
| HMI | 192.168.10.40 | Operator interface |
| Engineering PC | 192.168.10.100 | Programming and diagnostics |

These are example addresses only. Use the plant's approved address plan and check that the addresses are not already assigned.

### 3.2 Subnet mask

The subnet mask determines which addresses belong to the local IP subnet.

For the example network:

PLC IP: 192.168.10.10

Subnet mask: 255.255.255.0

Remote I/O IP: 192.168.10.20

The PLC and remote I/O are in the same IPv4 subnet under this configuration.

If two devices are connected to the same switch but use incompatible IP addressing, they may not communicate properly. Physical connectivity does not correct a subnet mismatch.

### 3.3 Default gateway

The default gateway is used when traffic must travel outside the local subnet.

For a standalone machine network whose devices communicate only within the same subnet, a default gateway may not be needed. In a routed plant network, the gateway must follow the approved addressing design.

An incorrect gateway can prevent communication with devices on other subnets while local communication still works.

### 3.4 Static addressing and DHCP

Industrial devices may obtain their addresses using static configuration or dynamic assignment.

Static addressing is often used for fixed machine devices because the address remains predictable.

DHCP allows a server to assign network parameters dynamically. The resulting address behavior depends on the DHCP configuration and device implementation.

BOOTP/DHCP tools are commonly encountered with certain Rockwell devices during initial setup. BOOTP and DHCP are related but distinct address-assignment mechanisms. Confirm the procedure supported by the exact device.

For fixed automation equipment, document the assigned address and ensure it will not conflict with another device or be unintentionally reassigned.

### 3.5 Address-planning checklist

Obtain the approved machine or plant subnet.

Record the intended IP address for every device.

Verify subnet masks and gateways.

Check for duplicate addresses before connecting the devices to the live network.

Record the MAC address where available.

Confirm VLAN and routing requirements.

Update the electrical drawing and network inventory.

Keep the addressing plan with the machine backup.

## 4. Configure and Verify Device IP Settings

The exact steps depend on the device.

### Common configuration methods

Rotary or DIP switches on supported devices.

BOOTP/DHCP configuration utilities.

Vendor device configuration software.

A device's web interface.

Controller or engineering software, where supported.

A supported device display or keypad.

### Recommended procedure

1.	Read the device manual and identify the supported address-setting method.

2.	Record the device's existing address and identity.

3.	Confirm the intended address against the approved network plan.

4.	Apply the address, subnet mask, and gateway as required.

5.	Follow the device's instructions for applying settings or restarting, if required.

6.	Verify the address through the device's configuration interface.

7.	Test IP connectivity from an approved workstation on the correct network.

8.	Confirm that the expected device identity responds, rather than assuming any response at that IP belongs to the intended device.

Do not reset a device to factory defaults merely because its address is unknown. Doing so may erase other configuration and create a much larger recovery job.

### Useful Windows commands

Display the PC's network configuration:

ipconfig /all

Test basic IP reachability:

ping 192.168.10.20

Inspect the local IPv4 neighbor cache:

arp -a

These commands help with initial diagnosis but do not validate every aspect of EtherNet/IP communication.

A failed ping does not conclusively prove that the device is offline. ICMP may be disabled or filtered.

A successful ping does not prove that a CIP connection or I/O exchange is working.

An ARP entry may help identify the responding interface, but it does not by itself establish the device's complete identity.

## 5. EDS Files: Electronic Data Sheets

An Electronic Data Sheet (EDS) is a device description file used by compatible engineering tools to identify an industrial device and describe supported configuration and communication information.

In EtherNet/IP engineering, an EDS can help software recognize a device and present its identity, parameters, and supported capabilities.

### 5.1 What an EDS file can describe

Depending on the device and EDS implementation, it may contain information such as:

Vendor identification.

Device type and product code.

Product name and revision information.

Communication capabilities.

Supported parameters and configuration options.

Information used by engineering software to construct or validate device configuration.

The engineering tool and device still determine which features are actually supported. An EDS file does not make an otherwise incompatible device compatible.

### 5.2 EDS versus other configuration files

| Item | Purpose |
| --- | --- |
| EDS file | Describes device identity and supported capabilities to compatible tools |
| PLC project | Contains controller program and associated project configuration |
| I/O configuration | Defines controller-side devices and communication relationships |
| Firmware | Software executed by the device hardware |
| Device parameter backup | Stores device-specific settings, where the device and tools support it |
| Network drawing | Documents physical topology, addresses, and connections |
| Switch configuration backup | Stores applicable switch settings such as VLANs and port configuration |

These items are not interchangeable. Keeping only the EDS does not provide a complete system backup.

### 5.3 Obtaining the correct EDS

1.	Identify the exact manufacturer and device catalog number.

2.	Confirm the product revision and supported firmware.

3.	Obtain the EDS from the manufacturer's approved source or software package.

4.	Check the file identity and compatibility notes.

5.	Register or install the EDS using the applicable engineering tool's procedure.

6.	Confirm that the software recognizes the expected device.

7.	Verify the actual device and connection settings before downloading configuration changes.

Avoid random EDS downloads from unrelated websites. A device description that appears similar may refer to a different product revision or a different communication interface.

### 5.4 What if the EDS is missing?

Possible symptoms include:

The device is shown as an unknown or unrecognized device.

The engineering tool cannot display the expected device-specific configuration.

A generic device entry is used instead of a detailed profile.

Device-specific configuration or validation features are unavailable.

A missing EDS does not necessarily mean the physical network is broken. A device may still respond to IP-level tests or support some communication functions. The exact impact depends on the tool, device, and engineering workflow.

### 5.5 What if the EDS is incorrect?

An incorrect EDS may cause the engineering tool to display misleading identity or configuration information, or it may prevent the intended device profile from being used.

Check:

Vendor ID and product code.

Device type.

Product revision and compatibility.

Device identity reported by the actual hardware.

The source and version of the EDS.

Whether the selected engineering profile matches the installed device.

Do not change the hardware configuration merely to make it match an incorrect device description.

## 6. Controller and I/O Configuration

After basic IP communication is verified, configure the device in the controller project using the supported engineering software.

In Rockwell environments, this commonly involves Studio 5000 Logix Designer for supported Logix controllers, together with device-specific tools where required.

### 6.1 Typical configuration elements

Controller type and firmware revision.

Ethernet communication interface.

Device identity and network address.

I/O module or device profile.

Connection type and data format.

Input and output assembly information, where applicable.

Requested Packet Interval.

Connection size and supported configuration parameters.

Device-specific configuration data.

The exact fields depend on the device and the software version.

### 6.2 Device identity and compatibility

The controller project must describe a device that matches the actual hardware and its supported communication behavior.

If the catalog number, revision, connection type, or data format is incorrect, the controller may fail to establish the intended connection even though the device is reachable over IP.

For a replacement device, confirm whether the existing project profile supports the new hardware revision. Do not assume that matching the product family name is sufficient.

### 6.3 Assembly instances and data sizes

Many EtherNet/IP devices use assembly objects to group I/O data. A device may provide separate assemblies for input data, output data, and configuration data.

The required assembly instances and sizes are device-specific.

Before configuring them, check the manufacturer's documentation for:

Input assembly instance.

Output assembly instance.

Configuration assembly instance, if required.

Expected data size.

Supported connection types.

Any required configuration data.

An incorrect assembly instance or data size can cause a connection failure or incorrect data interpretation. Never copy these values from another drive or I/O adapter just because the models look similar.

## 7. Requested Packet Interval (RPI)

The Requested Packet Interval (RPI) defines the requested update period for a supported CIP connection.

For example, an RPI of 10 ms requests an update period of 10 milliseconds for that connection. It does not mean that the entire machine reacts within 10 milliseconds.

### 7.1 Why RPI matters

RPI affects how frequently data is requested to be transferred for the connection. Its suitability depends on the control requirement and the capabilities of the controller, device, and network.

Common considerations include:

Required control response.

Device-supported RPI range.

Number of connections.

Input and output data size.

Controller and communication-module capacity.

Network load and topology.

Task execution and device processing times.

Connection watchdog and fault behavior.

### 7.2 Choosing an RPI

Use the device manual and the controller's supported configuration limits to choose a suitable value.

A useful engineering approach is:

1.	Identify how quickly the control system needs fresh data.

2.	Check the device's supported update interval and connection limits.

3.	Review the controller's task timing and communication capacity.

4.	Consider the number of connected devices and the size of their data.

5.	Configure an RPI that satisfies the application without creating unnecessary network load.

6.	Validate the actual connection and machine response under realistic operating conditions.

Do not automatically assign the shortest possible RPI to every device. More frequent updates can increase network and controller load without improving the physical process.

### 7.3 Example RPI values

| Example RPI | Nominal requested interval | General interpretation |
| --- | --- | --- |
| 2 ms | 2 milliseconds | Fast requested updates, only where supported and justified |
| 10 ms | 10 milliseconds | A relatively frequent update request |
| 20 ms | 20 milliseconds | A less frequent update request |
| 100 ms | 100 milliseconds | A slower update request, potentially suitable for less time-sensitive data |

These are illustrative values, not universal recommendations. The supported minimum and practical performance depend on the specific controller, device, connection type, and network design.

### 7.4 RPI and network load

A simplified conceptual relationship is:

More frequent updates generally increase the rate of communication packets.

Larger data payloads increase the amount of data transferred per update.

More active connections increase the overall communication workload.

The actual traffic also includes Ethernet, IP, UDP, and other protocol overhead, plus any additional messaging. Therefore, multiplying payload size by update frequency alone will underestimate total network traffic.

### 7.5 RPI versus task period

The PLC task period and the RPI are different parameters.

| Parameter | Role |
| --- | --- |
| RPI | Requested interval for a CIP connection's data updates |
| Periodic task period | Configured execution interval for a periodic PLC task |
| Program execution time | Time required to execute the relevant controller logic |
| Device processing time | Time for the device to process incoming or outgoing data |
| Physical response time | Time for the actual process or mechanism to respond |

These timing elements interact. Setting an RPI lower than a task period does not automatically make the control logic execute more frequently.

### 7.6 Connection status and RPI

A device can have a valid IP address but still have an invalid I/O connection because of:

An unsupported RPI.

An incompatible connection type.

Incorrect assembly instances or data sizes.

A device profile or firmware mismatch.

Resource limitations.

Incorrect connection configuration.

Network communication faults.

When changing an RPI, verify the resulting connection status and actual data behavior. A configured value alone does not prove that the connection is operating as intended.

## 8. Unicast, Multicast, and Switch Configuration

EtherNet/IP connections may use unicast or multicast delivery, depending on the device and connection configuration.

### Unicast

Unicast traffic is directed to a specific destination. It is commonly used in point-to-point communication and supported I/O configurations.

### Multicast

Multicast traffic is directed to a group of receivers. It can allow multiple configured consumers to receive the same produced data stream.

Multicast traffic needs suitable network handling. Managed switches may use IGMP snooping to limit multicast forwarding to ports that need the traffic. Some designs also require an IGMP querier.

During setup, verify:

VLAN membership and port configuration.

Switch port status and errors.

Whether the device connection uses unicast or multicast.

IGMP snooping and querier configuration, if required.

Whether network segmentation or security controls block necessary traffic.

Do not change multicast or VLAN settings on a live production network without understanding the existing design. A seemingly minor switch change can interrupt several machines at once.

## 9. Common Setup Errors

| Mistake | Likely result | Corrective action |
| --- | --- | --- |
| Duplicate IP address | Intermittent or incorrect device communication | Identify both devices and assign unique approved addresses |
| Wrong subnet mask | Local communication or routing problems | Compare the mask with the approved network plan |
| Incorrect gateway | Communication with other subnets fails | Verify the approved routing configuration |
| Wrong device profile | Configuration or connection failure | Match the profile to the actual device and revision |
| Missing or incorrect EDS | Device recognition or configuration difficulties | Obtain and register the correct device description |
| Incorrect assembly instance | I/O connection fault or incorrect data layout | Verify device-specific documentation |
| Incorrect data size | Connection establishment failure or data interpretation problems | Match the required assembly size |
| Unsupported RPI | Connection rejected or timing-related problems | Select a supported interval based on requirements |
| Wrong IP entered in the controller project | Controller targets the wrong device or cannot connect | Compare the project with the device's actual address |
| Switch VLAN mismatch | Device unreachable despite physical link | Verify VLAN membership and intended network path |
| Multicast not forwarded correctly | Some consumers miss I/O updates | Inspect multicast configuration and switch diagnostics |
| Configuration changes not saved | Settings are lost or cannot be restored | Save verified project and device configuration backups |

## 10. Worked Example: PLC to Remote I/O Adapter

Assume a Logix PLC exchanges data with an EtherNet/IP remote I/O adapter.

### Example network plan

| Parameter | PLC | Remote I/O |
| --- | --- | --- |
| IP address | 192.168.10.10 | 192.168.10.20 |
| Subnet mask | 255.255.255.0 | 255.255.255.0 |
| Default gateway | According to plant design | According to plant design |
| Device role | Controller | I/O adapter |
| Configuration source | Controller project | Device documentation and supported profile |

The addresses are examples. Use the actual plant addressing scheme when commissioning equipment.

### Setup procedure

1.	Confirm the exact controller and remote I/O adapter models.

2.	Check firmware compatibility and supported EtherNet/IP connection types.

3.	Assign or verify the approved IP addresses.

4.	Confirm that both devices use the intended subnet.

5.	Verify physical Ethernet links and switch-port status.

6.	Test basic IP reachability from an appropriately connected workstation.

7.	Obtain and register the correct EDS if required by the engineering workflow.

8.	Add or verify the remote I/O device in the controller project.

9.	Confirm the device identity, connection type, and required input/output data configuration.

10.	Set an RPI supported by the device and suitable for the application.

11.	Download or apply configuration using the approved commissioning procedure.

12.	Check the controller's I/O connection status and relevant device diagnostics.

13.	Verify that input data changes correctly when the physical input changes.

14.	Verify output operation using the approved test procedure and suitable feedback.

15.	Save the verified controller project, network configuration, and device records.

### If ping succeeds but the I/O connection fails

Do not start by replacing the Ethernet cable. Check the layers separately:

1.	Verify the IP address and the actual identity of the responding device.

2.	Check controller-side device identity and revision compatibility.

3.	Confirm the connection type, assembly instances, and data sizes.

4.	Verify that the RPI is supported.

5.	Review controller and adapter diagnostics.

6.	Check relevant switch and network behavior.

7.	Correct the identified issue and validate actual I/O data.

## 11. Commissioning and Documentation Checklist

### Before commissioning

Hardware catalog numbers and firmware versions recorded.

Approved IP address plan available.

Duplicate-address checks completed.

Subnet, gateway, and VLAN requirements verified.

EDS source and device compatibility verified.

Controller project and current configuration backed up.

Connection type and I/O data layout checked.

RPI selected from supported settings and application requirements.

Approved machine isolation and commissioning procedures available.

### During commissioning

Ethernet link and switch-port status verified.

IP configuration confirmed.

Basic connectivity tested.

Device identity confirmed.

Controller connection status checked.

Actual input and output data verified.

Device diagnostics reviewed.

Communication stability observed under realistic operating conditions.

Fault behavior verified where required by the approved test plan.

### After commissioning

Controller project saved.

EDS and device description records retained.

IP address inventory updated.

Network diagram updated.

Device parameters and relevant switch settings backed up.

Commissioning results documented.

Outstanding faults and limitations recorded.

Recovery procedure and spare-part details updated.

## 12. Industrial Maintenance and Retrofit Considerations

For a maintenance team, EtherNet/IP setup information should be stored as part of the machine's technical record.

For each installed device, maintain:

Machine and panel identification.

Device function and physical location.

Manufacturer and catalog number.

Firmware and hardware revision.

IP address, subnet, and gateway where applicable.

MAC address, where available.

EDS or other required device-description version.

Controller project and connection configuration.

RPI and relevant I/O assembly settings.

Switch port and VLAN information.

Backup location and recovery procedure.

Approved replacement part and compatibility notes.

This is particularly valuable when a remote I/O adapter, drive, or communication module fails during a breakdown. The objective is to reproduce a known-good configuration, not to reconstruct the entire network from memory while production waits.

Safety note: EtherNet/IP is a control communication technology, not a substitute for a validated safety system. Standard I/O communication should not be assumed to provide safety-rated behavior. Safety-related functions require suitable certified components, architecture, and validation according to the machine's safety requirements.

## 13. Interview Questions and Answers

### Q1. What are the main steps in setting up EtherNet/IP?

Identify compatible hardware, plan IP addresses, configure the devices, verify basic network connectivity, configure device descriptions and controller connections, select a supported RPI, test I/O data, and save the verified configuration.

### Q2. What is the purpose of an EDS file?

An EDS describes a device's identity and supported configuration or communication capabilities for compatible engineering tools. It helps the tool recognize and configure the device.

### Q3. Does installing an EDS configure the device's IP address?

Not necessarily. An EDS is a device description. IP configuration is handled through the addressing method supported by the device, such as static settings, BOOTP/DHCP, or a vendor utility.

### Q4. What is RPI?

RPI is the Requested Packet Interval for a supported CIP connection. It specifies the requested data-update period, subject to device, controller, and network capabilities.

### Q5. What happens if the RPI is too short?

It may increase network and controller communication load and may be unsupported by the device or connection. Select the interval according to the application requirement and documented limits.

### Q6. Why can a device respond to ping but show an I/O fault?

Ping verifies basic IP reachability. An I/O connection also depends on compatible device identity, connection configuration, data layout, RPI, and successful CIP communication.

### Q7. What is the difference between an IP address and a MAC address?

An IP address provides logical addressing at the IP layer. A MAC address identifies an Ethernet interface at the local network layer. ARP helps map an IPv4 address to a MAC address on the local network.

### Q8. What should be checked before replacing an EtherNet/IP device?

Verify the catalog number, firmware, network address, device profile, EDS requirements, supported connection types, I/O data layout, and configuration backup. Confirm that the replacement is compatible with the existing controller project.

### Q9. Does the shortest RPI always provide the best performance?

No. A shorter RPI requests more frequent updates but can increase communication load. The best setting meets the control requirement while remaining within the system's supported capabilities.

### Q10. What is the difference between an EDS and a PLC project?

An EDS describes a device for compatible engineering tools. A PLC project contains controller logic and associated project configuration. Neither replaces a complete backup of all device settings and network infrastructure.

## 14. Final Mental Model

Remember EtherNet/IP setup as five connected tasks:

1.	Addressing: Make sure each device has the correct, unique IP configuration.

2.	Identification: Ensure the engineering tool recognizes the correct device and revision.

3.	Connection configuration: Define compatible devices, connection types, and I/O data layouts.

4.	Timing: Choose an RPI that meets the application requirement and is supported by the system.

5.	Validation: Verify real data exchange, device behavior, fault status, and recoverable backups.

The critical commissioning distinction is that correct IP settings establish the possibility of communication; they do not prove that the CIP connection or machine I/O is working correctly.

## NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\03_Comms\03_Protocols\11_EtherNet_IP\03_Troubleshooting - Troubleshooting: Connection faults, duplicate IP