# 02_PLAN_WISE_2026\02_INDUSTRY3_0\06_Machine_Integ\01_Integration_Chain\02_PLC - PLC: Logic and control

## 1. Purpose of the PLC in Machine Integration

A Programmable Logic Controller (PLC) is an industrial control system that reads input signals, executes a control program, and updates outputs to operate a machine or process.

In machine integration, the PLC connects sensors, operator interfaces, drives, actuators, robots, safety-related systems, and production-level communication systems into a coordinated sequence.

The PLC determines what the machine should do based on its operating mode, process conditions, commands, interlocks, timers, counters, and fault states.

Typical responsibilities include:

Reading sensor signals and operator commands.

Executing automatic and manual operating sequences.

Controlling motors, VFDs, solenoid valves, contactors, and actuators.

Monitoring permissives and process conditions.

Managing alarms, faults, and recovery sequences.

Exchanging data with HMIs, robots, CNCs, SCADA systems, and other PLCs.

Recording production counts, cycle times, and process states.

Supporting diagnostics, traceability, and maintenance.

A PLC does not automatically make a machine safe simply because it is industrial-grade. Standard control logic and safety-related control functions must be distinguished and implemented using appropriate architectures.

## 2. Position of the PLC in the Machine Architecture

Physical process

|

v

Sensors and field devices

|

v

Electrical wiring and field I/O

|

v

PLC input interface

|

v

PLC control program

|

+----> HMI and operator commands

|

+----> VFDs and motor commands

|

+----> Pneumatic and hydraulic actuators

|

+----> Robot and CNC interfaces

|

+----> Alarms and production data

|

v

Machine movement or process action

|

v

Sensors confirm the result

|

v

PLC evaluates the next step

This architecture represents a feedback-controlled machine sequence. The PLC issues a command, then uses feedback to determine whether the intended action occurred.

For example, the PLC may command a cylinder to extend. It should not assume that the cylinder has extended merely because the solenoid output is ON. It should evaluate the appropriate position feedback and timeout conditions.

## 3. Main PLC Hardware Components

### 3.1 CPU

The Central Processing Unit executes the PLC program and manages control operations.

Typical CPU responsibilities include:

Program execution.

Memory management.

Input and output data processing.

Communication with field devices and networks.

Diagnostics and fault reporting.

Task scheduling and execution monitoring.

Retentive data handling, where supported and configured.

Important CPU specifications include program and data memory, supported instructions, execution performance, communication capacity, task capabilities, supported I/O systems, and environmental ratings.

### 3.2 Power supply

The PLC power supply provides the required operating power to the controller or rack.

Do not confuse the PLC's internal power supply with the field-device supply. Sensors, contactors, solenoids, and other devices may require separate 24 VDC or other supplies.

A fault in a shared field supply can cause several sensors or outputs to fail simultaneously even when the CPU remains healthy.

### 3.3 Digital input modules

Digital input modules detect discrete electrical states from devices such as:

Proximity sensors.

Push buttons.

Limit switches.

Relay contacts.

Auxiliary contacts.

Digital status outputs from drives.

Input-module compatibility depends on voltage, current, electrical topology, common arrangement, filtering, and isolation.

### 3.4 Digital output modules

Digital outputs control compatible electrical loads or interface devices.

Typical applications include:

Interposing relays.

Solenoid valves.

Contactor coils, where the output rating and interface are suitable.

Indicator lamps.

Drive digital inputs.

Output technologies include transistor, relay, and other module-specific designs.

Before connecting a load, verify output voltage, current, inrush, inductive-load requirements, switching frequency, and protection requirements.

### 3.5 Analog I/O modules

Analog inputs measure continuous signals such as 0–10 V or 4–20 mA.

Analog outputs generate continuous control signals, such as a speed reference to a compatible drive.

Verify signal range, resolution, channel configuration, isolation, wiring, scaling, and fault diagnostics.

### 3.6 Communication interfaces

Communication interfaces connect the PLC to devices such as:

Remote I/O.

VFDs and servo drives.

HMIs.

Robots.

CNC controllers.

Industrial switches.

SCADA and data collection systems.

Examples of industrial communication technologies include EtherNet/IP, PROFINET, Modbus TCP, Modbus RTU, and IO-Link through a suitable master.

The physical network and protocol are different concepts. Ethernet describes a family of networking technologies, while the industrial protocol defines how application data is exchanged.

## 4. PLC Operating Cycle and Task Execution

A conventional cyclic PLC task repeatedly evaluates its program. A simplified model is:

Start task cycle

|

v

Read or update input data

|

v

Execute control logic

|

v

Update output data

|

v

Perform communication and diagnostics

|

v

Repeat

This is a conceptual model. Actual PLC architectures differ. Some controllers use scheduled tasks, event-driven execution, immediate I/O instructions, distributed I/O updates, asynchronous communication, or multiple execution rates.

### 4.1 Scan time

Scan time is the time required for a defined program execution cycle or task execution, according to the controller's architecture.

It can be affected by:

Program size and complexity.

Instruction execution cost.

Communication processing.

Interrupts and higher-priority tasks.

I/O updates.

Online monitoring and diagnostics.

Controller loading.

The exact meaning of scan time depends on the platform and task configuration.

### 4.2 Why scan time matters

Suppose a physical input produces a pulse that is shorter than the time between relevant input samples. A conventional cyclic task may never observe the pulse.

Possible solutions include:

Using a suitable input filter configuration.

Using a hardware latch or pulse-capture feature.

Using a high-speed counter.

Using an interrupt or event task supported by the controller.

Selecting an appropriate input module.

For high-speed motion or pulse counting, do not assume that an ordinary digital input and ordinary cyclic logic are sufficient.

### 4.3 Response time

The total response time includes more than program execution time.

A simplified relationship is:

Tresponse=Tsensor+Tinput+Tcommunication+Tlogic+Toutput+Tactuator

The relevant terms depend on the system architecture. For remote I/O or networked drives, communication and update intervals may contribute significantly.

For a time-critical function, calculate or measure the complete path rather than using CPU scan time alone.

## 5. PLC Programming Languages

IEC 61131-3 defines commonly used PLC programming language approaches. The exact languages and features supported depend on the platform and software version.

| Language | Typical use | Main strength |
| --- | --- | --- |
| Ladder Diagram (LD) | Interlocks, discrete logic, maintenance-oriented control | Visual contact and coil representation |
| Function Block Diagram (FBD) | Signal processing and interconnected function blocks | Clear functional relationships |
| Structured Text (ST) | Calculations, data handling, complex conditions | Text-based logic and structured algorithms |
| Sequential Function Chart (SFC) | Step-based sequences | Explicit sequence organization |
| Instruction List (IL) | Legacy systems and older codebases | Compact instruction representation |

Instruction List is a legacy language in modern IEC 61131-3 editions. Existing installations may still contain older instruction-based programs.

### 5.1 Ladder Diagram

Ladder logic resembles relay control diagrams, using logical conditions and output instructions.

Conceptual example:

|----[ Start_PB ]----[ Safety_OK ]----[/ Fault ]----( Run_Request )----|

This example represents a logical condition, not a complete or validated machine safety circuit.

The symbols commonly represent:

[ condition ]: A true condition in the rung.

[/ condition ]: A logically negated condition.

( output ): An output instruction or Boolean assignment, depending on the PLC platform.

An instruction such as [/ Fault ] does not establish a safety-rated function. It only represents software logic.

### 5.2 Structured Text

Structured Text is useful for calculations, state management, data processing, and complex conditional logic.

Illustrative IEC-style pseudocode:

IF Auto_Mode AND Start_Request AND Permissives_OK THEN

Run_Request := TRUE;

ELSE

Run_Request := FALSE;

END_IF;

Actual syntax, variable declarations, task behavior, and supported instructions vary by platform.

### 5.3 Choosing a programming approach

Use the language that makes the control behavior clear, maintainable, and compatible with the engineering team's standards.

For example:

Use ladder logic for straightforward interlocks and discrete conditions when it suits the platform and team.

Use structured text for complex calculations and structured data manipulation.

Use function blocks for reusable functions and signal-processing structures.

Use sequence-oriented methods when they improve visibility of step transitions and recovery behavior.

A project may use multiple languages. Consistent naming, clear interfaces, and documented behavior matter more than using a single language everywhere.

## 6. PLC Variables, Tags, and Addressing

A PLC program operates on variables representing input states, output commands, process values, internal flags, timers, counters, and structured data.

### 6.1 Common variable categories

| Variable category | Example | Purpose |
| --- | --- | --- |
| Physical input | Part_Sensor_Input | Represents an input channel |
| Process tag | Part_Present | Represents interpreted process state |
| Command | Cylinder_Extend_Cmd | Requests an action |
| Feedback | Cylinder_Extended_FB | Confirms the physical state |
| Permissive | Auto_Permissives_OK | Indicates required conditions are satisfied |
| Alarm | Cylinder_Extend_Timeout | Reports an abnormal condition |
| Timer state | Extend_Timer_Done | Indicates a timer condition |
| Counter | Good_Part_Count | Tracks production quantity |
| Analog value | Hydraulic_Pressure | Stores a process measurement |
| State variable | Sequence_Step | Identifies the current sequence state |

### 6.2 Physical address versus symbolic tag

A physical address identifies a hardware channel or data location according to the PLC platform.

A symbolic tag gives the signal a meaningful name.

For example:

Physical input: I0.3 on a platform that uses this address format.

Symbolic tag: Part_Present_Input.

Process interpretation: Part_Present.

The address is only an example. Other PLCs use different addressing models, and some modern systems emphasize symbolic tags instead of direct physical addresses.

### 6.3 Raw input and interpreted process state

It is useful to separate raw hardware signals from process meaning.

Physical input channel

|

v

Raw input tag

|

v

Validation and interpretation

|

v

Process state

|

v

Sequence logic

This separation makes diagnostics clearer.

For example, a raw sensor input may be ON while the interpreted Part_Present state remains false because the program applies an additional validation condition. The program should make this behavior understandable and documented.

## 7. Boolean Logic and Interlocks

Boolean logic determines whether conditions are true or false.

### 7.1 AND

An AND condition is true only when all required conditions are true.

Y=A∧B

Example: A clamp command is permitted only when automatic mode is active and the station is ready.

### 7.2 OR

An OR condition is true when at least one specified condition is true.

Y=A∨B

Example: A warning may be generated when either a low-pressure condition or a high-temperature condition is detected.

### 7.3 NOT

NOT reverses a Boolean state.

Y=¬A

Example: A sequence may require NOT Cylinder_Extended_FB before starting an extension command.

Logical inversion must be used carefully. An OFF input can mean normal, abnormal, unpowered, disconnected, or simply not detected, depending on the circuit.

### 7.4 Interlocks

An interlock prevents an operation unless required conditions are satisfied.

Examples include:

Preventing a clamp from closing while a required access condition is not met.

Preventing a spindle-start command when required process permissives are missing.

Preventing two incompatible actuator commands from being active simultaneously.

Preventing automatic operation when the machine is in manual mode.

Preventing sequence advancement when the expected feedback has not arrived.

Interlocks should have a clearly defined purpose and should be documented.

### 7.5 Permissive versus interlock

The terms are sometimes used differently across companies, so project documentation should define them.

A permissive is generally a condition that must be satisfied before an action is allowed.

An interlock is generally a condition that prevents or interrupts an action when a prohibited or unacceptable state exists.

The same condition may be described differently by different engineering teams. Consistency within the project is the important part.

## 8. PLC Commands and Physical Feedback

A command and its corresponding feedback are different signals.

For example:

Motor_Run_Cmd: The PLC requests motor operation.

Drive_Ready_FB: The drive reports readiness.

Drive_Running_FB: The drive reports running status.

Motor_At_Speed_FB: The process confirms the required speed condition, if available.

A command does not prove that the physical action occurred.

The command may fail because of a drive fault, missing power, a disconnected cable, an actuator fault, a communication failure, or a missing permissive inside the drive.

### 8.1 Command-feedback comparison

| Command | Expected feedback | Possible fault interpretation |
| --- | --- | --- |
| Motor start | Drive running | Start failure or feedback issue |
| Cylinder extend | Extended sensor ON | Motion timeout or sensor fault |
| Clamp close | Clamp-closed feedback | Clamp did not reach position |
| Conveyor index | Position reached | Motion or position-detection failure |
| Pump start | Running status and/or process response | Drive, motor, or process fault |

The feedback must be selected according to the actual equipment and control requirements.

## 9. PLC Sequence Control

A machine sequence coordinates operations in a defined order.

Consider a station that detects a component, clamps it, performs a process, releases it, and waits for the next component.

Step 0: Wait for part

|

v

Step 10: Verify permissives

|

v

Step 20: Command clamp

|

v

Step 30: Confirm clamp position

|

v

Step 40: Execute process

|

v

Step 50: Confirm process completion

|

v

Step 60: Release clamp

|

v

Step 70: Confirm release

|

v

Return to Step 0

This is a conceptual sequence. Actual steps, transition conditions, and recovery behavior must be defined for the machine.

### 9.1 Sequence state

A sequence state identifies the current operation or step.

Examples include:

Waiting for a part.

Checking station readiness.

Clamping.

Processing.

Releasing.

Completing the cycle.

Recovering from a fault.

A state-based sequence is often easier to diagnose than a large collection of loosely related flags.

### 9.2 Transition conditions

A transition determines when the sequence moves to the next state.

A transition may depend on:

Sensor feedback.

Timer completion.

Operator confirmation.

Drive status.

Robot or CNC handshake.

Quality-result availability.

Fault-free conditions.

Transitions should be explicit and testable.

### 9.3 Sequence timeouts

A timeout detects that an expected event has not occurred within the permitted duration.

For example, if a cylinder extension is expected to finish within a configured time, the PLC can generate a timeout alarm if the extended feedback does not arrive.

A timeout should lead to a defined response. Depending on the machine, this may include stopping the sequence, inhibiting further movement, retaining diagnostic information, or requesting operator intervention.

Do not use a timeout as a substitute for proper safety design.

### 9.4 Recovery behavior

A robust sequence defines what happens after:

An interrupted cycle.

Loss of power.

PLC restart.

Drive fault.

Communication failure.

Sensor disagreement.

Emergency stop activation.

Operator reset.

The correct recovery behavior depends on the machine's hazards, mechanical state, process state, and restart requirements.

Automatic resumption should never be assumed to be appropriate.

## 10. Modes of Operation

Industrial machines commonly use several operating modes.

| Mode | Typical purpose | Main consideration |
| --- | --- | --- |
| Automatic | Executes the production sequence | Requires defined permissives and sequence control |
| Manual | Allows individual operator-requested actions | Must respect required interlocks and safety functions |
| Setup | Supports adjustment and commissioning | May require restricted movement and specific authorization |
| Maintenance | Supports service activities | Must follow isolation and safe-work procedures |
| Recovery | Restores the machine from a known fault state | Requires explicit recovery conditions |
| Simulation | Tests logic without normal physical operation | Must prevent simulated states from being mistaken for real feedback |

The mode architecture should make it clear which commands are allowed in each mode.

A manual mode must not be treated as permission to bypass safety requirements.

## 11. Timers, Counters, and Edge Detection

### 11.1 Timers

Timers support time-based control and monitoring.

Common timer concepts include:

On-delay: output becomes active after the input condition remains true for the configured interval.

Off-delay: output remains active for a configured interval after the triggering condition changes, depending on timer behavior.

Pulse timer: output remains active for a specified duration.

Retentive timer: accumulated time may be retained when the enabling condition becomes false, according to implementation.

Exact timer behavior and instruction names vary by PLC platform.

Applications include:

Cylinder travel timeout.

Debounce or delay validation.

Process dwell time.

Alarm delay.

Conveyor settling time.

### 11.2 Counters

Counters track events or quantities.

Typical applications include:

Good-part count.

Reject count.

Cycle count.

Component feed count.

Maintenance usage count.

For accurate counting, the program must identify the event that represents one valid count.

If a sensor remains ON for several PLC scans, a simple increment instruction may count the same part repeatedly unless the logic detects a new transition or otherwise prevents duplicate counting.

### 11.3 Rising-edge detection

A rising edge occurs when a Boolean signal changes from false to true.

Conceptually:

Previous_State = FALSE

Current_State  = TRUE

|

v

Rising_Edge = TRUE for one detected transition

A rising-edge instruction or equivalent logic can create a one-cycle pulse when a signal becomes active.

However, edge detection does not fix a pulse that the PLC never sampled. Fast events may require suitable hardware capture or high-speed input functions.

### 11.4 Debouncing

Mechanical contacts may produce multiple rapid transitions when they change state. This is called contact bounce.

A debounce method requires the signal to remain stable for a defined interval before accepting the new state.

Use filtering appropriate to the application. Excessive debounce time can cause missed events or unacceptable response delays.

## 12. Analog Processing and Engineering Units

The PLC may receive a raw digital representation of an analog input rather than a value already expressed in engineering units.

For example, a pressure transmitter may deliver 4–20 mA, which is converted by the analog input module into a raw value.

The PLC program then scales that value to the desired unit, such as bar.

For a linear signal:

PV=LRV+Raw−RawminRawmax−Rawmin(URV−LRV)

Where:

PV is the engineering value.

LRV and URV are the lower and upper engineering limits.

Raw is the measured input representation.

Rawmin and Rawmax are the raw values corresponding to the configured range.

The raw limits must match the actual module configuration. They should not be assumed to be identical across PLC families.

### 12.1 Analog validation

A good analog-processing routine considers:

Under-range and over-range conditions.

Open-circuit diagnostics where supported.

Sensor fault indications.

Plausibility limits.

Scaling correctness.

Filtering requirements.

Engineering-unit display.

Behavior when the value is invalid.

Do not silently convert an invalid sensor value into a normal process value.

## 13. PLC Output Control and Interfacing

A PLC output instruction represents a control decision. It does not necessarily supply the voltage or current needed to operate every field load directly.

The interface must match the load.

Examples include:

Interposing relays for suitable control circuits.

Contactors for motor power switching.

Solenoid valves for pneumatic or hydraulic functions.

VFD digital inputs for run commands.

Analog outputs for compatible speed references.

Industrial networks for drive commands and status data.

Check output ratings, load current, inrush current, inductive switching behavior, isolation, and protective components.

For inductive loads, suitable suppression may be required. The correct suppression device depends on the load type, voltage, switching requirements, and manufacturer instructions.

## 14. PLC-to-VFD Control Interface

A PLC can command a VFD through hardwired signals or an industrial communication interface.

### 14.1 Hardwired interface

A simple interface may include:

PLC digital output to drive run input.

PLC analog output to drive speed-reference input.

Drive-ready feedback to a PLC digital input.

Drive-running feedback to a PLC digital input.

Drive-fault feedback to a PLC digital input.

This approach can be straightforward to troubleshoot, but it requires suitable wiring and configuration.

### 14.2 Networked interface

A networked interface may exchange:

Start and stop commands.

Speed or frequency reference.

Drive status word.

Actual frequency or speed.

Fault codes.

Ready and running states.

Parameter or diagnostic information, where supported.

Networked control requires compatible protocol configuration, addressing, data mapping, and fault-response handling.

The PLC and drive must agree on command ownership and control mode. A correctly programmed PLC command will not work if the drive is configured to accept commands from a different source.

## 15. PLC-to-Robot and PLC-to-CNC Handshaking

When integrating a PLC with a robot or CNC controller, both systems must agree on signal meanings and sequence ownership.

Typical handshake signals include:

Ready.

Start request.

Busy.

Cycle complete.

Fault.

Reset request.

Part available.

Part accepted.

Process result.

A conceptual handshake is:

PLC checks machine permissives

|

v

PLC sends start request

|

v

Robot or CNC accepts request

|

v

Robot or CNC reports busy

|

v

Process executes

|

v

Robot or CNC reports completion

|

v

PLC validates completion and advances sequence

Actual handshake behavior must be defined by the interface specification. Some systems require the request to remain active until acknowledgment; others use different protocols.

### 15.1 Handshake design rules

Define the meaning of every signal.

Define which controller owns each command.

Specify whether a signal is maintained or pulsed.

Define acknowledgment and completion conditions.

Define timeout behavior.

Define behavior after communication loss.

Prevent duplicate command execution.

Define reset and recovery behavior.

Verify that both systems use compatible signal polarity and data mapping.

A single Start bit without a defined acknowledgment and completion protocol is often insufficient for reliable machine integration.

## 16. Alarms, Faults, and Diagnostics

A useful PLC fault-management design distinguishes between the physical symptom, the detected condition, the machine response, and the recovery method.

Examples:

Sensor failed to activate within the permitted time.

Drive reported a fault.

Communication with remote I/O was lost.

Analog value is outside the valid range.

Robot did not acknowledge a request.

Required process pressure was not reached.

Sequence entered an unexpected state.

### 16.1 Alarm structure

A practical alarm record may contain:

| Field | Purpose |
| --- | --- |
| Alarm ID | Unique identification |
| Alarm text | Clear description of the condition |
| Trigger condition | Logic that activates the alarm |
| Severity | Relative operational importance |
| Timestamp | When the event occurred |
| Machine state | Relevant sequence or operating mode |
| Recommended check | Action for diagnosis |
| Reset condition | Conditions required for clearing |
| Historical status | Whether the event is retained for review |

### 16.2 Alarm versus trip

The exact definitions vary by company, but commonly:

An alarm informs the operator about an abnormal condition.

A trip stops or inhibits an operation according to the defined control response.

Some conditions require both an alarm and a trip. A message displayed on an HMI does not itself guarantee that the machine has entered a safe state.

### 16.3 Fault latching

Some faults remain recorded until the cause is cleared and an authorized reset condition is met.

Fault latching can preserve evidence of a transient event and prevent automatic continuation after an abnormal condition.

However, not every fault should be latched identically. The behavior must be selected according to the fault's purpose and the machine's recovery requirements.

## 17. PLC Communication and Remote I/O

Remote I/O places input and output modules near the machine equipment while the PLC exchanges data over an industrial network.

Benefits can include reduced home-run wiring and more modular machine architecture.

Potential failure points include:

Incorrect IP address or device name.

Network cable or connector damage.

Incorrect protocol configuration.

Duplicate addressing.

Incorrect I/O assembly or data mapping.

Wrong module configuration.

Device firmware or compatibility issues.

Network load or update-time problems.

Lost connection or stale data.

### 17.1 Communication status

The PLC should use appropriate communication diagnostics to determine whether remote data is valid.

A network connection indicator alone does not prove that the correct process data is being exchanged.

Verify:

Device identity.

Configured I/O size.

Connection status.

Update interval.

Input and output mapping.

Device fault status.

Data validity and quality indicators where supported.

### 17.2 Communication-loss response

Define what the machine should do if the PLC loses communication with a remote I/O station, drive, robot, or CNC.

The response depends on the device and hazard analysis. It may include inhibiting new commands, stopping a process, reporting a fault, or entering a defined recovery state.

Do not assume that every networked device automatically transitions to the required machine state after communication loss.

## 18. PLC Program Structure and Maintainability

A maintainable program makes the control behavior easy to understand, test, and diagnose.

A useful high-level structure may be:

Main Program

|

+---- Input and signal processing

|

+---- Mode management

|

+---- Permissives and interlocks

|

+---- Machine sequence

|

+---- Drive and actuator control

|

+---- Robot and CNC handshakes

|

+---- Alarm and fault management

|

+---- HMI and communication data

|

+---- Diagnostics and maintenance data

This is a conceptual organization, not a required PLC architecture.

### 18.1 Naming conventions

Use names that communicate function and state.

Examples:

Part_Present

Clamp_Close_Cmd

Clamp_Closed_FB

Conveyor_Run_Cmd

Drive_Ready

Drive_Fault

Sequence_Step

Cycle_Complete

Pressure_Valid

A consistent naming scheme reduces confusion between commands, feedback, status, alarms, and calculated conditions.

### 18.2 Avoid unexplained internal flags

Internal flags are sometimes necessary, but excessive unnamed or poorly documented flags make fault tracing difficult.

For each important flag, determine:

What does it represent?

Where is it set?

Where is it reset?

Is it retentive?

Can more than one routine modify it?

What happens after a restart?

Does the HMI display or depend on it?

The objective is to make the program's behavior explainable, not merely functional.

## 19. PLC Backup, Version Control, and Change Management

A working PLC program is an engineering asset. Uncontrolled changes can introduce downtime, quality defects, and safety risks.

A suitable change-management process includes:

1.	Identify the correct controller and program version.

2.	Obtain an approved baseline backup.

3.	Record the proposed change and its purpose.

4.	Assess machine, process, safety, and quality impacts.

5.	Develop and test the change in an appropriate environment.

6.	Obtain required authorization.

7.	Implement the change using the approved procedure.

8.	Verify actual machine behavior.

9.	Update the as-built program, drawings, tag lists, and relevant documents.

10.	Store the new baseline with version information and change history.

A backup should be more than a file with a plausible name. Confirm that it belongs to the correct machine, controller, software version, hardware configuration, and approved revision.

Where supported, record checksums, version identifiers, firmware information, and relevant configuration details.

## 20. PLC Commissioning Checklist

### 20.1 Hardware and wiring

Verify PLC model, CPU, firmware, and I/O module configuration.

Check supply voltage and grounding arrangements.

Confirm I/O channel assignments against approved drawings.

Verify field wiring, common terminals, and polarity.

Confirm output load ratings and interface devices.

Verify network connections and device identity.

Check that safety-related components are installed according to the approved design.

### 20.2 Program and configuration

Confirm the correct program and revision are loaded.

Verify tag mapping and physical I/O correspondence.

Check task configuration and execution diagnostics.

Confirm timers, counters, and analog scaling.

Verify mode selection and permissives.

Confirm alarms, fault latching, and reset behavior.

Check communication configuration and data mapping.

### 20.3 Functional validation

Test each input against the actual field device.

Test outputs using the approved commissioning method.

Verify command-feedback relationships.

Test normal automatic sequences.

Test manual and setup functions.

Test timeout and fault conditions.

Test communication-loss behavior where required.

Verify restart and recovery behavior.

Validate required safety functions independently according to the approved safety plan.

Record results and update as-built documentation.

## 21. PLC Troubleshooting Method

Use a structured method to isolate the fault instead of changing several variables at once.

### Step 1: Define the symptom

Identify exactly what is not working.

Examples:

PLC input does not change.

Output command remains OFF.

Output command is ON but the actuator does not move.

Sequence is stuck at a step.

Drive is ready but does not start.

HMI shows a value that differs from the field measurement.

### Step 2: Identify the last known correct point

Follow the signal path from field device to controller and from controller to actuator.

Field device

|

v

Electrical signal

|

v

PLC I/O channel

|

v

Program tag

|

v

Interlock or sequence condition

|

v

Output command

|

v

Output hardware

|

v

Actuator or drive

### Step 3: Compare command and feedback

Determine whether the problem is:

A missing command.

A missing feedback signal.

A command that was issued but not accepted.

A physical action that failed.

Incorrect interpretation of an otherwise valid signal.

### Step 4: Check controller diagnostics

Review CPU status, I/O faults, task execution, communication health, drive diagnostics, and relevant alarms.

### Step 5: Test one hypothesis at a time

Use measurements, program monitoring, approved test procedures, and device diagnostics to establish the cause.

### Step 6: Verify the correction

Confirm that the original symptom is resolved and that normal sequence operation, fault handling, and relevant safety functions remain correct.

## 22. Common PLC Integration Failures

| Symptom | Possible cause | First diagnostic direction |
| --- | --- | --- |
| Input always OFF | Supply, wiring, topology, sensor, or channel fault | Measure at the device and input terminal |
| Input always ON | Short circuit, incorrect polarity, sensor state, or wiring fault | Compare field signal and module state |
| Output command ON, load inactive | Output module, interface, supply, wiring, or load fault | Check output voltage and load circuit |
| Sequence stuck | Missing transition condition or fault state | Monitor the current step and required conditions |
| Drive does not start | Missing permissive, wrong command source, fault, or interface mismatch | Check PLC command and drive status |
| Incorrect analog value | Scaling, wiring, configuration, or transmitter problem | Compare raw value with a reference measurement |
| Duplicate production counts | Repeated scan-level counting without event detection | Review edge detection and count conditions |
| Intermittent operation | Noise, loose wiring, unstable supply, or timing issue | Check physical signal quality and diagnostics |
| Remote I/O unavailable | Network, addressing, configuration, or device fault | Verify device identity and connection diagnostics |
| Unexpected restart behavior | Retained state or recovery logic issue | Review startup and state-initialization design |

These are diagnostic possibilities, not definitive diagnoses. Confirm the cause before modifying the program or replacing hardware.

## 23. Practical Example: PLC-Controlled Clamping Station

Consider a station that detects a part, clamps it, and signals readiness to a robot.

### Inputs

Part_Present

Clamp_Closed_FB

Clamp_Open_FB

Robot_Ready

Robot_Cycle_Complete

Station_Fault

### Commands

Clamp_Close_Cmd

Clamp_Open_Cmd

Robot_Start_Request

Station_Ready

### Conceptual sequence

Idle

|

| Part_Present and required permissives

v

Clamp command

|

| Clamp_Closed_FB

v

Station ready

|

| Robot_Ready

v

Robot start request

|

| Robot_Cycle_Complete

v

Release clamp

|

| Clamp_Open_FB

v

Cycle complete

|

v

Return to Idle

The actual implementation must define how commands are maintained, how the robot acknowledges a start request, and how the station responds to missing feedback.

### Required fault handling

Part not detected.

Clamp fails to close.

Clamp feedback signals disagree.

Robot is not ready.

Robot does not acknowledge or complete the cycle.

Communication is lost.

A required permissive becomes false during operation.

An unexpected state is detected.

The station should not report readiness merely because the clamp-close output is ON. It should verify the conditions defined by the control design.

## 24. Interview Questions and Answers

1\. What is a PLC?

A PLC is an industrial controller that processes input data, executes a control program, and updates outputs to control a machine or process.

2\. What is a PLC scan cycle?

It is a defined cycle or scheduled execution in which the controller processes input data, executes logic, and updates outputs. The exact execution model depends on the platform and task configuration.

3\. What is scan time?

Scan time is the duration of a specified program execution cycle or task execution. Its meaning depends on the controller architecture.

4\. What is the difference between an input and an internal tag?

An input represents a hardware or communication input state. An internal tag may represent a calculated condition, command, state, timer, counter, or process interpretation.

5\. What is the difference between a command and feedback?

A command requests an action. Feedback indicates the reported or measured state of the equipment or process.

6\. What is an interlock?

An interlock prevents or interrupts an operation when a defined condition makes that operation prohibited or unacceptable.

7\. What is a permissive?

A permissive is a condition that must be satisfied before an operation is allowed.

8\. Why are timers used in PLC logic?

Timers implement delays, process dwell times, and timeouts that detect whether an expected condition occurs within a defined interval.

9\. Why is edge detection useful?

It identifies a transition, such as OFF to ON, and can generate a single event for counting or sequence logic.

10\. Why might a PLC miss a short sensor pulse?

The pulse may be shorter than the effective input sampling or filtering interval. A suitable high-speed input, hardware capture, or other supported feature may be required.

11\. What is a state-based sequence?

It is a control approach in which the machine occupies a defined state and moves to another state when specified transition conditions are satisfied.

12\. How should a PLC detect a failed cylinder movement?

Use suitable position feedback and a defined timeout. If the expected feedback does not arrive within the permitted time, the program should initiate the specified fault response.

13\. What is the difference between a standard PLC and a safety PLC?

A standard PLC performs general machine control. A safety PLC is designed and certified for defined safety-related applications when used within an appropriate safety architecture and validated implementation.

14\. What is remote I/O?

Remote I/O places input and output modules near field equipment and communicates their data to the controller over a supported network.

15\. What should be checked when a PLC output is ON but an actuator does not operate?

Check the output hardware, supply, wiring, interface relay or drive, load condition, protection devices, and the actuator itself.

16\. Why is alarm management important?

It helps operators and maintenance personnel identify abnormal conditions, understand their impact, and follow a defined recovery procedure.

17\. Why is program version control necessary?

It establishes which program is approved, supports controlled changes, and enables reliable recovery from an incorrect or unsuccessful modification.

18\. Why is a communication-loss response necessary?

A controller must know how to respond when remote devices or data become unavailable. The required behavior depends on the machine design and associated risks.

19\. What is the difference between hardwired and networked drive control?

Hardwired control uses electrical signals for commands and feedback. Networked control exchanges command and status data through a configured communication protocol.

20\. What is the most important principle in PLC troubleshooting?

Trace the complete signal path, identify the last known correct point, compare commands with feedback, and verify the cause before making changes.

## 25. Engineering Principles to Remember

The PLC coordinates the machine, but its outputs do not prove that physical actions have occurred.

Separate raw I/O, interpreted process states, commands, feedback, permissives, and alarms.

Design sequences with explicit states, transitions, timeouts, and recovery behavior.

Ensure that task execution and I/O capabilities meet the required response time.

Use compatible electrical interfaces and properly configured communication.

Define command ownership and handshake behavior when integrating drives, robots, and CNCs.

Treat fault handling and restart behavior as part of the control design.

Keep programs, drawings, tag lists, backups, and configuration records synchronized.

Test normal operation and abnormal conditions using an approved commissioning procedure.

Implement safety-related functions through an appropriate validated safety architecture, not merely standard PLC logic.

## NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\06_Machine_Integ\01_Integration_Chain\03_VFD - VFD: PLC commands start and speed