# PLC Battery Maintenance

## 1. Definition

A PLC battery is a battery used in certain programmable logic controller systems to support specific backup functions when the normal power supply is unavailable. Depending on the PLC design, it may preserve battery-backed memory, retained data, a real-time clock, or other functions specified by the manufacturer.

Not every PLC contains a battery. Modern controllers may use nonvolatile memory, flash storage, capacitors, or other technologies to retain programs and data without a replaceable battery.

Important distinction: A PLC battery does not necessarily power the CPU or keep the control program executing during a power failure. Its function depends on the controller architecture.

PLC battery maintenance is part of preventive maintenance because a depleted or failed battery can compromise supported backup functions and complicate recovery after a power interruption.

## 2. Objectives of PLC Battery Maintenance

Detect low-battery warnings before backup capability is lost.

Maintain the required retention of battery-backed memory or data.

Preserve real-time clock accuracy where the battery supports it.

Prevent avoidable loss of retained information.

Replace batteries according to manufacturer requirements.

Confirm that the correct battery type is installed.

Prevent damage caused by leakage, incorrect polarity, or unsuitable replacement parts.

Maintain readiness for power interruptions and controller recovery.

Document battery condition, replacement date, and relevant controller information.

## 3. Why PLCs Use Batteries

The battery function depends on the controller's design.

| Possible function | Purpose | Important limitation |
| --- | --- | --- |
| Memory backup | Supports retention of specified memory areas | Does not necessarily preserve every data area |
| Real-time clock backup | Maintains date and time during loss of normal power | Clock behavior depends on the controller design |
| Retained data support | Preserves designated data when normal power is removed | Retention rules vary by CPU and memory architecture |
| Specialized backup function | Supports a manufacturer-defined function | Must be verified in the exact hardware manual |

Some controllers use batteries only for the clock, while others use them for additional backup functions. Certain modern PLCs have no user-replaceable battery at all.

Never assume that every PLC battery preserves the program. Check the exact CPU model and its memory-retention design.

## 4. PLC Battery Versus Other Power and Memory Components

| Component | Primary purpose | Typical maintenance concern |
| --- | --- | --- |
| PLC backup battery | Supports specified backup functions | Low voltage, depletion, incorrect replacement |
| PLC power supply | Provides operating power to the controller system | Voltage instability, overload, overheating, failure |
| Capacitor-based backup | Provides temporary energy for supported retention functions | Aging, loss of hold-up capability, manufacturer-defined replacement |
| Nonvolatile memory | Retains stored information without continuous power | Data integrity, storage faults, configuration and backup management |
| Removable memory card | Stores supported programs, configurations, or data | Compatibility, integrity, access, and retention requirements |

A power-supply failure and a battery failure can produce different symptoms. Diagnosing one as the other can lead to unnecessary replacement and unreliable recovery.

## 5. Common PLC Battery Technologies

### 5.1 Lithium primary batteries

Some PLCs use non-rechargeable lithium batteries for backup functions.

Typical characteristics:

Long service life under specified conditions.

Low self-discharge compared with many other primary battery chemistries.

Manufacturer-defined voltage and capacity.

Specific storage and replacement requirements.

Potential leakage or damage if mishandled or used incorrectly.

The exact chemistry and construction must be confirmed from the approved part specification.

### 5.2 Rechargeable backup batteries

Some older or specialized systems use rechargeable batteries.

Their maintenance requirements may include manufacturer-defined charging behavior, service-life limits, and replacement procedures.

Do not substitute a non-rechargeable battery for a rechargeable type or vice versa unless the manufacturer explicitly approves the substitution.

### 5.3 Controllers without replaceable batteries

Many modern PLCs rely on nonvolatile memory and other retention mechanisms.

For these systems, maintenance may focus on:

Backup verification.

Memory and storage diagnostics.

Real-time clock behavior.

Controller health.

Manufacturer-defined retention requirements.

Do not create a battery replacement task for a controller that does not use a replaceable battery.

## 6. Battery-Related Failure Symptoms

Possible indications of a battery-related problem include:

Low-battery or battery-fault indication.

A diagnostic entry identifying battery voltage or backup status.

Loss or incorrect retention of a supported data area.

Real-time clock reset or incorrect time after power loss.

Manufacturer-specific backup-memory warnings.

A battery that has exceeded its prescribed service-life limit.

These symptoms do not prove that the battery is the root cause. A clock problem, for example, may arise from configuration or another hardware issue.

### 6.1 Common diagnostic distinction

| Symptom | Possible causes |
| --- | --- |
| Battery warning appears | Battery depletion, poor contact, incorrect battery type, or battery-monitoring fault |
| PLC program missing after power loss | Memory-retention design, backup problem, memory fault, incorrect restoration, or battery-related failure on a battery-dependent system |
| Clock resets after power loss | Battery issue, clock backup design, configuration, or controller-specific behavior |
| PLC restarts unexpectedly | Power supply, electrical disturbance, controller fault, or another underlying issue |
| Retained data changes or disappears | Retention configuration, program logic, memory design, battery issue where applicable, or incorrect restoration |

Use the diagnostic information and controller documentation to narrow the cause before replacing components.

## 7. Battery Health Indicators

Battery monitoring differs by PLC family. Some controllers provide a dedicated LED, while others display a diagnostic message in engineering software or on an operator interface.

Possible indicators include:

Battery LED or battery-status indicator.

CPU diagnostic message.

Engineering-software warning.

Hardware diagnostic event.

Maintenance notification.

Manufacturer-defined battery-life or replacement indication.

The meaning of an indicator depends on the specific controller.

For example, a red LED does not have a universal meaning across PLC manufacturers. Read the relevant hardware manual rather than applying one controller's interpretation to another.

## 8. PLC Battery Preventive Maintenance Procedure

### Step 1: Identify the controller

Record:

Machine and equipment identification.

PLC manufacturer and CPU model.

CPU part number and firmware version where relevant.

Battery part number, if fitted.

Manufacturer's replacement requirements.

Current battery diagnostic status.

Confirm the battery function from the hardware manual.

### Step 2: Review battery condition

Check:

Battery warnings.

Diagnostic buffer entries.

Previous replacement records.

Manufacturer-defined service-life requirements.

Environmental conditions.

Any known retention or clock problems.

Do not wait for an actual loss of retained information before responding to a valid low-battery warning.

### Step 3: Verify the correct replacement

Confirm:

Exact approved part number.

Voltage and chemistry.

Physical connector and polarity.

Compatibility with the CPU.

Storage and shelf-life requirements.

Whether replacement must occur with the CPU powered.

The manufacturer's specified replacement procedure.

A battery that physically fits may still be electrically or functionally unsuitable.

### Step 4: Prepare the replacement

Before starting:

Read the CPU-specific replacement instructions.

Confirm that the replacement part is approved and within its usable storage period.

Verify that the correct controller and battery compartment have been identified.

Preserve the approved PLC project and required data backups.

Confirm the machine's operating condition and maintenance authorization.

Determine whether the procedure requires the PLC to remain powered or be shut down.

Do not automatically power off the PLC before replacing the battery. Some older controllers require a specific powered replacement procedure to maintain backup functions, while other systems require isolation. The manufacturer's instructions and site safety procedures determine the correct method.

### Step 5: Replace the battery

Follow the exact controller-specific procedure.

Observe polarity and connector orientation.

Avoid short-circuiting the battery terminals.

Avoid electrostatic discharge damage to electronic components.

Do not force connectors or battery holders.

Avoid touching exposed circuitry unnecessarily.

Handle and dispose of the removed battery according to applicable site and environmental requirements.

Never improvise a battery replacement on an operating PLC simply because an online procedure describes another model.

### Step 6: Verify the result

After replacement, perform the checks specified by the manufacturer.

These may include:

Confirming that the battery warning has cleared.

Checking CPU and module diagnostics.

Verifying the real-time clock where relevant.

Confirming the expected retention of supported data.

Checking the PLC operating state.

Confirming that the program and hardware configuration remain correct.

Performing required functional checks.

Recording any unresolved warning or diagnostic event.

Do not clear a warning and assume the problem is resolved without confirming the underlying condition.

## 9. Powered Versus Unpowered Battery Replacement

This is one of the most important details in PLC battery maintenance.

### 9.1 Replacement with power maintained

Some battery-dependent controllers permit battery replacement while the CPU remains powered. This may allow supported backup functions to remain available during the replacement process.

However:

The procedure is controller-specific.

Only authorized and qualified personnel should perform the work.

Electrical and mechanical hazards must still be controlled.

The battery compartment and accessible components must be handled as specified.

The required time limit, if any, must be observed.

### 9.2 Replacement with power removed

Other systems require power isolation or have no requirement to keep the controller energized during replacement.

In such cases, verify how the program, retained data, and clock are preserved. Confirm that the approved project and required configuration are available before starting.

### 9.3 Decision rule

| Controller condition | Correct approach |
| --- | --- |
| Manual explicitly requires powered replacement | Follow that procedure under the required authorization and safety controls |
| Manual explicitly requires isolation | Isolate and replace according to the procedure |
| Controller has no replaceable battery | Follow its nonvolatile-memory and backup maintenance requirements |
| Replacement procedure is unknown | Identify the exact CPU and obtain the correct manufacturer instructions before proceeding |

There is no universal rule that all PLC batteries must be replaced with power ON or power OFF.

## 10. PLC Program and Data Retention

Battery maintenance must be understood in the context of the controller's memory architecture.

### 10.1 Program memory

The control program may be stored in nonvolatile memory or another manufacturer-specific storage arrangement. Battery failure may not affect program retention on systems designed to preserve the program without a battery.

### 10.2 Retained data

Retained data may include:

Counters.

Production totals.

Recipe-related values.

Selected internal variables.

State information.

Other application data explicitly configured for retention.

Not all PLC variables are retained. The program, memory configuration, controller architecture, and firmware determine which data survives power loss.

### 10.3 Real-time clock

The clock may depend on a battery or another backup mechanism. Incorrect time can affect:

Event timestamps.

Diagnostic-buffer interpretation.

Production records.

Time-based sequences.

Data historian correlation.

Maintenance event investigations.

If the clock is incorrect, correct it using the approved procedure and verify synchronization with relevant HMI, SCADA, and server systems.

### 10.4 Backup is still necessary

A battery is not a substitute for an approved PLC backup.

Maintain suitable copies of:

PLC application.

Hardware configuration.

Relevant communication configuration.

Device parameters.

Required retained-data exports, where supported and appropriate.

Safety-related project information under its applicable controlled process.

Verify backup identity, integrity, version, and restoration requirements.

## 11. Battery Maintenance in Siemens PLCs

Siemens SIMATIC controllers differ substantially across generations. Some older systems use batteries or battery-dependent backup arrangements, while many newer controllers use nonvolatile memory for application retention.

### 11.1 Maintenance approach

Identify the exact CPU model and hardware revision.

Check the relevant Siemens operating instructions.

Confirm whether a replaceable battery is fitted.

Determine which functions depend on it.

Check battery diagnostics and replacement requirements.

Verify any manufacturer-defined replacement procedure.

Confirm program, data, and clock behavior after replacement.

### 11.2 Siemens S7-1500

Do not assume that an S7-1500 CPU requires a conventional replaceable backup battery. Its memory and retention design must be checked for the specific CPU and associated hardware.

For an S7-1500 installation, prioritize the documented memory-retention architecture, approved project backup, diagnostic information, and any manufacturer-defined backup components or procedures.

### 11.3 Legacy Siemens systems

Some legacy SIMATIC systems use battery-backed functions or battery-dependent memory arrangements.

For these systems, verify the battery type, supported retention functions, replacement procedure, and consequences of loss of backup power from the specific manual.

## 12. Battery Maintenance in Allen-Bradley PLCs

Allen-Bradley controller families differ in their use of batteries, nonvolatile memory, removable storage, and other retention mechanisms.

### 12.1 Maintenance approach

Identify the exact ControlLogix, CompactLogix, or other controller model.

Check the applicable hardware manual.

Determine whether a replaceable battery is fitted.

Verify the battery's intended backup function.

Review the controller's battery and memory diagnostics.

Confirm the correct replacement part.

Follow the model-specific replacement procedure.

Verify the application and required data after maintenance.

### 12.2 Important distinction

A controller's ability to retain an application or recover from power loss depends on its hardware architecture and supported storage arrangement.

Do not assume that all ControlLogix or CompactLogix controllers use the same battery or that battery replacement is required on every model.

## 13. Battery Maintenance in Mitsubishi PLCs

Mitsubishi MELSEC PLCs include multiple generations and CPU families with different memory and backup arrangements.

### 13.1 Maintenance approach

Identify the exact MELSEC CPU model.

Consult the applicable hardware manual.

Confirm whether the CPU or associated module uses a battery.

Check the battery diagnostic indication or error history.

Verify the correct battery part number.

Follow the manufacturer's replacement instructions.

Check program, retained data, and clock behavior as specified.

Record the replacement and verification results.

The requirements for an older MELSEC CPU may differ significantly from those of a newer model. Model-specific instructions take priority over general maintenance practices.

## 14. Battery Storage, Handling, and Disposal

Battery quality can deteriorate before installation if storage conditions are unsuitable.

### 14.1 Storage

Follow the manufacturer's storage temperature and humidity limits.

Respect shelf-life and date-code requirements.

Keep batteries in suitable packaging.

Prevent short circuits by protecting terminals.

Separate damaged or suspect batteries.

Maintain stock rotation and inventory records.

Do not install a battery with unknown history when traceability is required.

### 14.2 Handling

Confirm polarity before installation.

Do not short-circuit or disassemble batteries.

Do not recharge primary batteries.

Do not heat, crush, puncture, or incinerate batteries.

Do not mix incompatible battery chemistries.

Follow site procedures for damaged or leaking batteries.

### 14.3 Disposal

Dispose of used batteries through the site's approved battery-waste process and applicable local requirements.

Do not place industrial batteries into general waste where prohibited. Damaged lithium batteries may require additional precautions under the site's environmental and safety procedures.

## 15. Battery Replacement Records and SAP PM

Battery maintenance should be traceable in the plant's maintenance system.

The exact workflow depends on the site's SAP configuration and work-order procedures.

### 15.1 Useful maintenance records

Equipment or functional-location ID.

PLC manufacturer and CPU model.

Battery part number.

Previous replacement date.

Inspection date.

Battery warning or diagnostic condition.

Replacement date.

Removed battery condition, where relevant.

Installed battery identification or batch information where required.

Verification results.

Technician and work-order details.

Next inspection or replacement requirement.

Outstanding defects or follow-up actions.

### 15.2 SAP PM use

A typical process may include:

1.	Create or use the relevant maintenance notification.

2.	Identify the equipment and maintenance task.

3.	Plan the battery and any required resources.

4.	Execute the approved inspection or replacement.

5.	Record the actual work and materials consumed.

6.	Record the verification results.

7.	Update the equipment history.

8.	Schedule the next maintenance activity where required.

Do not assign an arbitrary universal replacement interval. Use the manufacturer's requirements and the plant's approved maintenance strategy.

## 16. Battery Maintenance KPIs

| KPI | Purpose |
| --- | --- |
| Battery warning count | Tracks detected battery-related conditions |
| Overdue battery inspections | Identifies missed preventive maintenance |
| Battery-related failure count | Tracks failures attributed to battery problems |
| Battery replacement compliance | Measures adherence to the approved maintenance schedule |
| Battery replacement cost | Tracks material and labor costs |
| Backup-related recovery incidents | Tracks events involving loss of supported backup functions |
| Clock synchronization issues | Identifies timestamp reliability problems where battery backup is relevant |
| Incorrect battery replacement incidents | Tracks compatibility, handling, or procedure failures |

These indicators are useful only when the plant has defined which PLC models require battery maintenance and what constitutes a battery-related failure.

## 17. Common PLC Battery Maintenance Mistakes

| Mistake | Consequence | Correct approach |
| --- | --- | --- |
| Assuming every PLC has a battery | Unnecessary maintenance and incorrect spare planning | Check the exact CPU design |
| Assuming the battery powers the CPU | Incorrect diagnosis of power-related faults | Separate backup functions from operating power |
| Assuming the battery always retains the program | False confidence in recovery capability | Verify the controller's memory architecture |
| Replacing the battery with an incompatible type | Backup failure or hardware damage | Use the approved battery specification |
| Powering off a CPU that requires powered replacement | Potential loss of supported backup functions | Follow the exact replacement procedure |
| Replacing a battery while the procedure requires isolation | Unacceptable electrical or equipment risk | Follow the approved safety and replacement instructions |
| Ignoring a low-battery warning | Loss of supported retention functions may occur | Investigate and replace as specified |
| Installing old or poorly stored stock | Reduced service life or unreliable backup | Check shelf life and storage conditions |
| Skipping verification | A failed or incorrect replacement may go unnoticed | Confirm the expected diagnostic and retention behavior |
| Relying only on the battery | Recovery may fail for unrelated reasons | Maintain and verify approved program and data backups |
| Failing to update maintenance records | Replacement history and future maintenance become unreliable | Record the work and required follow-up |

## 18. Practical Example: Battery Warning on a Legacy PLC

A production machine's legacy PLC displays a low-battery warning during a routine inspection. The machine is currently operating normally.

### Initial assessment

Identify the exact CPU model.

Read the battery diagnostic information.

Check the relevant hardware manual.

Confirm which functions depend on the battery.

Review the previous replacement record.

Confirm that the approved project and necessary recovery information are available.

### Replacement planning

The manual specifies that the battery must be replaced using a particular procedure to preserve the supported backup function.

The technician verifies the correct battery part number, prepares the approved replacement, confirms the required operating condition, and obtains the necessary authorization.

### Replacement and verification

Replace the battery according to the model-specific procedure.

Check the battery diagnostic status.

Verify the CPU's operating state.

Confirm clock or retained-data behavior where applicable.

Check relevant diagnostic information.

Record the part number, date, and verification results.

### Follow-up

The maintenance record is updated, and the next inspection or replacement activity is scheduled according to the approved maintenance plan.

The machine's normal operation before replacement did not prove that the battery remained healthy. The warning was an early indication that a supported backup function needed attention.

## 19. PLC Battery Maintenance Checklist

### Identification and planning

Exact PLC CPU and hardware version identified.

Presence and purpose of the battery confirmed.

Manufacturer's replacement requirements reviewed.

Correct replacement battery verified.

Approved project and required recovery information available.

Maintenance authorization and operating condition confirmed.

### Replacement

Correct powered or isolated replacement procedure followed.

Battery polarity and connection verified.

Electrostatic discharge precautions applied where required.

Removed battery handled and disposed of correctly.

No unauthorized hardware or program changes made.

### Verification and records

Battery diagnostic status checked.

CPU operating state checked.

Relevant clock and retained-data functions verified.

Required program and configuration integrity checks completed.

Outstanding warnings investigated.

Maintenance record updated.

Next required inspection or replacement activity scheduled.

## 20. Final Principles

A PLC battery supports only the backup functions specified by its controller design.

Not every PLC requires a replaceable battery.

Program retention, retained data, clock backup, and CPU operating power are different functions.

Manufacturer instructions determine the correct battery, replacement method, and maintenance interval.

Powered versus unpowered replacement must never be guessed.

Low-battery warnings should be addressed before supported backup functions are compromised.

A battery is not a substitute for a verified PLC project and data backup.

Post-replacement verification and maintenance records are essential.

Correct battery management improves recovery readiness and reduces avoidable maintenance risk.

Core principle: Identify what the battery actually protects, follow the exact CPU-specific replacement procedure, verify the required backup functions, and maintain a reliable record of the work.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\18_PM\01_PLC\04_Power_Supply - Power supply