# Network Fault: Physical Layer, Cables, Connectors and Fibre

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\19_Breakdown\06_Network_Fault\01_Physical_Layer

## 1. Purpose of Physical-Layer Troubleshooting

The physical layer is the foundation of industrial communication networks. It carries electrical or optical signals between PLCs, remote I/O, HMIs, CNCs, drives, industrial switches, robot controllers, SCADA systems, and other networked equipment.

A network can have correct IP addresses, valid PLC logic, and correctly configured devices but still fail because of a damaged cable, poor termination, loose connector, excessive electromagnetic interference, incorrect fibre type, or faulty transceiver.

Physical-layer faults can cause:

Complete communication loss.

Intermittent device disconnection.

PLC communication timeouts.

Remote I/O faults.

HMI data freezing or communication alarms.

Robot, CNC, or drive network alarms.

Packet loss and network retries.

Reduced communication performance.

Unstable communication that changes with vibration, temperature, or machine movement.

Core diagnostic principle: Verify the physical communication path before changing network configuration. Replacing IP addresses, resetting devices, or modifying PLC programs will not repair a broken conductor.

## 2. OSI Model and the Physical Layer

The Open Systems Interconnection (OSI) model divides communication into seven conceptual layers.

| Layer | Name | Industrial example |
| --- | --- | --- |
| 7 | Application | HMI data exchange, SCADA application |
| 6 | Presentation | Data representation and encoding |
| 5 | Session | Communication session management |
| 4 | Transport | TCP and UDP |
| 3 | Network | IP addressing and routing |
| 2 | Data Link | Ethernet frames, MAC addresses, switching |
| 1 | Physical | Cable, connector, electrical signal, fibre, transceiver |

The physical layer defines how bits are carried across a medium, including signal characteristics, connectors, pin assignments, transmission media, and applicable physical interfaces.

PLC / HMI / Drive / Remote I/O

↓

Network Interface / PHY

↓

RJ45 / Industrial Connector / Fibre Transceiver

↓

Copper Cable or Optical Fibre

↓

Switch / Network Device

↓

Receiving Interface

The actual network path may contain several switches, patch panels, connectors, and cable segments.

## 3. Important Physical-Layer Terminology

| Term | Meaning |
| --- | --- |
| PHY | Physical-layer transceiver circuitry |
| NIC | Network interface controller |
| Ethernet | Common wired networking technology |
| UTP | Unshielded twisted-pair cable |
| STP | Shielded twisted-pair cable, although manufacturers may use more specific shielding terminology |
| S/FTP | Cable construction with overall braid shielding and individually foil-shielded pairs |
| RJ45 | Common name for the 8-position modular connector used with Ethernet copper cabling |
| M12 | Circular industrial connector family, available in different codings |
| T568A / T568B | Standardized copper Ethernet wire termination arrangements |
| Pinout | Assignment of electrical signals to connector contacts |
| Attenuation | Reduction in signal strength along a transmission path |
| Crosstalk | Unwanted coupling between adjacent signal conductors |
| EMI | Electromagnetic interference |
| RFI | Radio-frequency interference |
| NEXT | Near-end crosstalk |
| Return loss | Measure related to signal reflection caused by impedance discontinuities |
| Insertion loss | Signal loss introduced by a cable, connector, or other transmission component |
| Optical fibre | Medium that carries information using light |
| Transceiver | Device or module that transmits and receives signals |
| SFP | Small Form-factor Pluggable transceiver module |
| OTDR | Optical Time-Domain Reflectometer, used to characterize fibre links and locate certain faults |
| Link loss | Loss of the physical connection between network interfaces |
| Intermittent fault | Fault that appears and disappears under changing conditions |

## 4. Common Industrial Ethernet Cable Types

### 4.1 Copper twisted-pair Ethernet

Copper Ethernet uses pairs of conductors twisted together to reduce electromagnetic coupling and crosstalk.

Common categories include:

Cat5e: Commonly used for 100BASE-TX and 1000BASE-T within the applicable channel specifications.

Cat6: Supports common Ethernet applications, with performance depending on the channel and installation requirements.

Cat6A: Designed to support 10GBASE-T over a compliant channel up to 100 metres.

Industrial Ethernet cable: Designed for environmental conditions such as vibration, oil exposure, flexing, temperature, or mechanical stress, depending on its construction.

Do not choose a cable based only on its category marking. Confirm the cable's industrial suitability, connector compatibility, shielding arrangement, transmission rate, and installation requirements.

### 4.2 Shielded and unshielded cables

| Feature | UTP | Shielded cable |
| --- | --- | --- |
| Construction | No metallic cable shield | Foil, braid, or a combination |
| EMI protection | Primarily from pair twisting and cable design | Adds shielding when correctly installed |
| Grounding considerations | No cable shield to bond | Requires correct shield termination and bonding |
| Installation | Often simpler | Requires attention to EMC and grounding practices |
| Typical use | Suitable environments with acceptable interference | Industrial environments where shielding is specified |

Important: Shielding is not a substitute for correct cable routing, grounding, bonding, or suitable cable construction. Incorrectly terminated shields can reduce EMC performance and may introduce other problems.

### 4.3 Straight-through and crossover cables

Traditional Ethernet installations sometimes use straight-through and crossover cables.

A straight-through cable has the same pin arrangement at both ends.

A crossover cable swaps the relevant transmit and receive pairs for applicable interfaces.

Auto-MDI/MDI-X allows many modern Ethernet ports to adapt automatically to either arrangement.

In industrial maintenance, use the cable type specified by the equipment manufacturer and site standard. Do not assume every industrial port supports Auto-MDI/MDI-X.

## 5. Ethernet Copper Wiring and Pinouts

### 5.1 T568A and T568B

T568A and T568B specify how the eight conductors are assigned to the eight contacts of a modular Ethernet connector.

| Pin | T568A conductor | T568B conductor |
| --- | --- | --- |
| 1 | White/Green | White/Orange |
| 2 | Green | Orange |
| 3 | White/Orange | White/Green |
| 4 | Blue | Blue |
| 5 | White/Blue | White/Blue |
| 6 | Orange | Green |
| 7 | White/Brown | White/Brown |
| 8 | Brown | Brown |

Use the wiring arrangement required by the cable design and site standard. Both ends terminated identically normally form a straight-through cable. The appropriate crossover arrangement differs according to the Ethernet application.

### 5.2 Common termination mistakes

One conductor is not fully inserted.

Incorrect conductor order.

Damaged contacts.

Excessive untwisting near the termination.

Cable jacket not properly secured.

Poor shield continuity.

Incorrect connector type for the cable construction.

Crimping a stranded conductor into a connector designed for solid conductors, or vice versa.

Mixing incompatible field-termination components.

A cable can pass a basic continuity test and still fail at higher data rates because continuity alone does not validate all transmission characteristics.

### 5.3 T568A versus T568B

T568A and T568B are both accepted termination schemes for applicable copper Ethernet cabling. A mixed termination at the two ends creates a crossover arrangement, but it is not automatically a fault. Whether it works depends on the equipment and Ethernet interface.

For industrial troubleshooting, confirm the intended cable design before reterminating it.

## 6. Industrial Connectors

### 6.1 RJ45 connectors

Common in control cabinets, engineering PCs, HMIs, PLCs, switches, and industrial Ethernet equipment.

Potential problems:

Broken locking tab.

Loose fit.

Bent or contaminated contacts.

Poor crimp.

Cable strain.

Damaged shield contact.

Oil, moisture, or dust ingress where protection is inadequate.

### 6.2 M12 connectors

M12 connectors are widely used in industrial environments because they provide a robust circular connection and may offer appropriate environmental protection.

Common Ethernet-related codings include:

D-coded: Commonly associated with 10/100 Mbit/s Industrial Ethernet connections.

X-coded: Designed for higher-speed Ethernet applications, including 10 Gbit/s in compliant systems.

The connector coding, pin assignment, cable, and equipment port must all be compatible. Never select an M12 cable based on connector shape alone.

### 6.3 Connector inspection checklist

1.	Verify connector type and coding.

2.	Inspect pins or contacts for damage.

3.	Check for contamination, moisture, and corrosion.

4.	Inspect the locking mechanism and coupling nut.

5.	Verify cable strain relief.

6.	Check shield termination where applicable.

7.	Confirm that the connector is fully seated and secured.

8.	Inspect the cable entry and seal for damage.

Do not disconnect or reconnect industrial communication connectors casually during active production. Some networks and machines may experience immediate loss of control or remote I/O if a link is interrupted.

## 7. Industrial Ethernet Cable Routing and EMC

Electrical noise can disrupt communication even when a cable appears physically undamaged.

### 7.1 Common sources of interference

Variable-frequency drives (VFDs).

Servo drives and motor cables.

Contactors and switching devices.

Welders.

High-current conductors.

Solenoid valves.

Poorly bonded electrical enclosures.

Improperly installed cable shields.

Grounding and bonding problems.

### 7.2 Good routing practices

Follow the machine builder's and plant's cable-routing standards.

Separate communication cables from high-noise power and motor cables where required.

Use specified crossing arrangements when communication and power cables must intersect.

Avoid unnecessary cable loops and excessive length.

Protect cables from sharp edges, hot surfaces, moving parts, and mechanical damage.

Use appropriate cable carriers for moving axes and robot dress packs.

Maintain minimum bend radius.

Use the correct shield termination and bonding method.

Keep connectors protected from oil, coolant, dust, and vibration as required by the environment.

### 7.3 Signs of EMI-related faults

Communication fails when a VFD starts.

Errors increase during welding.

Network interruptions occur only during certain machine cycles.

Communication becomes unstable when motors accelerate.

A cable works on a bench but fails after installation.

Errors change after cable routing or cabinet work.

Diagnostic approach: Correlate communication events with machine operating conditions. Inspect routing, bonding, shielding, and cable condition before changing network settings.

## 8. Optical Fibre Fundamentals

Optical fibre carries data as light rather than electrical signals. It provides electrical isolation and can support long distances or high bandwidth, depending on the fibre and transceivers used.

### 8.1 Main components

Optical transmitter.

Optical receiver.

Fibre transceiver or SFP module.

Optical fibre cable.

Connectors.

Splices and patch panels, where used.

Optical power monitoring, if supported.

### 8.2 Single-mode and multimode fibre

| Feature | Single-mode fibre | Multimode fibre |
| --- | --- | --- |
| Core | Smaller core | Larger core |
| Light propagation | One principal spatial mode | Multiple modes |
| Typical use | Longer-distance links | Commonly shorter-distance links |
| Transceiver compatibility | Requires matching single-mode optics | Requires matching multimode optics |
| Identification | Often marked OS1 or OS2 depending on cable type | Often marked OM1, OM2, OM3, OM4, or OM5 |

The achievable distance and speed depend on the complete optical link, including the fibre specification, transceiver wavelength, optical budget, connectors, splices, and equipment requirements.

### 8.3 Common fibre connector types

LC: Small form-factor connector frequently used with SFP modules.

SC: Push-pull connector used in many optical installations.

ST: Bayonet-style connector found in some legacy systems.

Connector type alone does not establish optical compatibility. Check fibre mode, connector polish, transceiver specification, wavelength, and the equipment manufacturer's requirements.

## 9. Fibre-Optic Safety and Handling

Optical fibre requires careful handling because damage can be difficult to see and fibre fragments can injure skin or eyes.

Never look directly into a fibre connector or optical transceiver.

Do not assume a fibre is inactive because no visible light can be seen.

Use approved inspection equipment and procedures.

Keep connector end faces clean and protected.

Do not touch optical end faces.

Follow the specified cleaning method.

Do not bend fibre below its minimum bend radius.

Avoid pulling, crushing, or twisting fibre cables.

Collect and dispose of broken fibre fragments using the approved procedure.

Use the correct connector inspection tools before mating connections.

Invisible infrared light may be present even when no visible red light is observed. Visual inspection by the naked eye is not a valid way to confirm optical safety or signal quality.

## 10. Fibre Faults and Troubleshooting

### 10.1 Common symptoms

Fibre link does not establish.

Link drops intermittently.

Optical receive power is too low.

Communication errors increase.

One direction of communication fails.

A link works with one transceiver but not another.

Fault appears after a cable is moved or a connector is cleaned.

### 10.2 Common causes

Incorrect fibre mode.

Incompatible transceiver wavelength.

Transmit/receive fibre strands reversed.

Dirty connector end face.

Damaged fibre.

Excessive bend or microbending.

Poor splice.

Excessive connector or splice loss.

Faulty SFP or optical transceiver.

Incorrect optical budget.

Incompatible connector polish or type.

### 10.3 Troubleshooting sequence

1.	Record the device and port reporting the fault.

2.	Confirm the fibre type and transceiver specifications at both ends.

3.	Check port status and supported optical diagnostics.

4.	Inspect connector condition using approved inspection equipment.

5.	Clean and reconnect according to the prescribed procedure.

6.	Confirm transmit and receive strand arrangement.

7.	Check receive optical power against the transceiver's supported limits.

8.	Use an optical power meter or OTDR where appropriate and authorized.

9.	Substitute a known-good compatible component only after documenting the original condition.

10.	Verify stable communication under normal machine operating conditions.

An OTDR can help locate certain events such as breaks, splices, and loss points, but it is not a replacement for checking transceiver compatibility and live receive-power specifications.

## 11. Copper Cable Testing

### 11.1 Basic continuity tester

A basic cable tester can identify:

Open conductors.

Short circuits.

Incorrect conductor mapping.

Reversed conductors.

Some split-pair and wiring errors, depending on the tester.

It cannot fully certify cable transmission performance.

### 11.2 Cable certifier

A cable certifier evaluates whether the installed cabling meets the selected cabling standard and performance category. Depending on the instrument and test, it may measure:

Wire map.

Insertion loss.

Return loss.

Near-end crosstalk.

Propagation delay.

Delay skew.

Other channel or permanent-link parameters.

### 11.3 Test method selection

| Tool | Best use | Limitation |
| --- | --- | --- |
| Basic cable tester | Quick wiring and continuity checks | Does not certify full transmission performance |
| Cable certifier | Validating compliance with a cabling standard | Requires correct test setup and selected limit |
| Digital multimeter | Selected electrical checks when the cable is isolated and safe | Not a substitute for Ethernet cable certification |
| Network switch diagnostics | Port link, speed, duplex, and some cable diagnostics | Features vary by switch model |
| Optical power meter | Measuring optical power | Does not independently identify every source of loss |
| OTDR | Locating certain fibre events and faults | Requires correct settings and interpretation |

Avoid applying a multimeter or other electrical test instrument to a connected, powered Ethernet port. Disconnect and isolate the cable as required before conducting tests that are not designed for live Ethernet circuits.

## 12. Common Physical-Layer Faults

| Symptom | Possible cause | First check |
| --- | --- | --- |
| No link light | Cable disconnected, broken cable, faulty port, or incompatible interface | Check seating, port status, and known-good cable |
| Link drops when the cable moves | Broken conductor, loose connector, or poor termination | Inspect connector and cable strain points |
| Intermittent network faults during machine motion | Flexing cable damage or EMI | Inspect moving cable, routing, and shielding |
| Fibre link remains down | Wrong fibre type, dirty connector, incompatible optics, or reversed strands | Verify compatibility and connector condition |
| Errors increase at higher speeds | Poor termination, cable category issue, or transmission impairment | Use suitable cable diagnostics or certification |
| Link works only over a short cable | Marginal cable, excessive loss, or defective interface | Test cable and compare with specifications |
| Communication fails near a VFD | EMI, routing, or bonding problem | Inspect EMC installation and correlate with VFD operation |
| One device disconnects repeatedly | Local port, connector, cable, or device interface fault | Check link status and substitute known-good components systematically |
| Fibre receive power is too low | Dirty connector, excessive loss, wrong optics, or damaged fibre | Check optical power and link specifications |
| Network fails after connector replacement | Incorrect pinout, poor termination, or incompatible connector | Verify cable construction, wiring, and connector compatibility |

## 13. Structured Physical-Layer Troubleshooting

Follow a repeatable method rather than replacing components at random.

Record Alarm and Affected Device

↓

Check Port and Link Status

↓

Inspect Cable and Connectors

↓

Confirm Cable / Connector Compatibility

↓

Check Routing, Shielding and Physical Damage

↓

Test Cable or Fibre Using the Correct Instrument

↓

Substitute a Known-Good Compatible Component if Needed

↓

Verify Stable Communication Under Operating Conditions

↓

Document Root Cause and Corrective Action

### Step 1: Capture the initial condition

Record:

Device name and network port.

Switch port, if applicable.

Alarm text and time.

Whether the fault is permanent or intermittent.

Machine operating state when the fault occurs.

Recent cable movement, maintenance, or component replacement.

### Step 2: Inspect physical connections

Check the cable route, connector seating, locking mechanism, visible damage, bend radius, and environmental exposure.

### Step 3: Confirm compatibility

Verify the correct cable type, connector coding, Ethernet speed capability, fibre mode, transceiver wavelength, and equipment requirements.

### Step 4: Check physical indicators

Observe link and activity LEDs, where provided. Check the switch port status and available diagnostic information.

LED meanings vary by manufacturer and device. Consult the device manual rather than assuming that every green or amber light has the same meaning.

### Step 5: Test the medium

Use the appropriate copper cable tester, cable certifier, optical power meter, or OTDR based on the suspected fault and required level of verification.

### Step 6: Verify the repair

Confirm the link remains stable during normal machine operation. For intermittent faults, include the operating conditions that previously triggered the failure.

## 14. Practical Industrial Breakdown Scenarios

### Scenario 1: PLC loses remote I/O communication intermittently

Observed condition: Remote I/O disconnects intermittently while the machine operates.

Investigation:

1.	Record PLC and remote I/O diagnostic information.

2.	Check switch-port link events.

3.	Inspect the cable and connectors at both ends.

4.	Check moving cable sections and cable carriers.

5.	Review routing near VFDs, servo drives, and high-current wiring.

6.	Test or substitute the suspected cable using compatible components.

Possible root causes: Intermittent conductor break, loose connector, poor termination, EMI, or faulty network interface.

Verification: Confirm stable I/O communication through the operating cycle that previously caused the fault.

### Scenario 2: Ethernet link is down after cable replacement

Observed condition: The device worked before maintenance but no longer establishes a link.

Investigation:

1.	Confirm both ends are seated correctly.

2.	Check the cable type and connector compatibility.

3.	Verify termination and pin mapping.

4.	Confirm that the new cable supports the required application.

5.	Check port status and substitute a known-good compatible cable if needed.

Possible root causes: Incorrect pinout, damaged termination, incompatible connector, or defective replacement cable.

Verification: Confirm link establishment and expected device communication.

### Scenario 3: Fibre communication fails after cabinet work

Observed condition: A fibre link remains down after a switch or transceiver is replaced.

Investigation:

1.	Confirm both transceivers are compatible.

2.	Verify fibre mode and wavelength.

3.	Check the connector type and condition.

4.	Confirm transmit and receive strands are correctly connected.

5.	Measure optical receive power if supported.

6.	Inspect the fibre for damage or excessive bending.

Possible root causes: Incorrect optical module, reversed strands, dirty end face, or damaged fibre.

Verification: Confirm the expected optical status and stable communication.

### Scenario 4: Network faults occur when a VFD starts

Observed condition: Communication errors coincide with motor acceleration.

Investigation:

1.	Record the timing of communication events.

2.	Inspect Ethernet cable routing relative to motor and drive cables.

3.	Check shield termination and bonding against site EMC standards.

4.	Inspect connector integrity and cable condition.

5.	Review drive installation and earthing practices.

6.	Verify communication stability after the installation issue is corrected.

Possible root causes: EMI coupling, poor bonding, damaged shielding, or incorrect cable routing.

Verification: Run the affected machine through the operating conditions that previously triggered the fault.

### Scenario 5: Ethernet communication fails only when a robot moves

Observed condition: A robot or machine network link drops at certain positions.

Investigation:

1.	Identify whether the cable moves with the robot.

2.	Inspect the dress pack, cable carrier, and bend points.

3.	Check for twisting, stretching, abrasion, or crushed sections.

4.	Inspect connectors for strain.

5.	Test the cable and replace it with the specified flex-rated cable if confirmed defective.

Possible root causes: Conductor fatigue, shield damage, connector strain, or unsuitable cable construction.

Verification: Validate the connection through the robot's required motion range.

## 15. Preventive Maintenance Checklist

### Copper Ethernet

Inspect cable jackets for cuts, crushing, abrasion, and oil damage.

Check connectors and locking tabs.

Verify correct cable routing and mechanical protection.

Inspect moving cable sections and strain-relief points.

Check for recurring link drops or port errors.

Verify cable replacement parts meet the required specification.

### Fibre optics

Check fibre routing and bend radius.

Inspect cable jackets and connector housings.

Protect disconnected fibre connectors from contamination.

Use approved inspection and cleaning procedures.

Verify compatible transceivers and fibre specifications.

Review optical power diagnostics where supported.

### EMC and installation

Check communication cable separation from high-noise power circuits.

Verify shield termination and bonding practices.

Inspect cabinet cable entries and grounding arrangements.

Check whether faults correlate with VFD, servo, welding, or robot activity.

Record recurring network interruptions and corrective actions.

## 16. Physical-Layer Breakdown Record Template

Machine / Line:

Device Name:

Device IP / Identifier:

Network Type:

Device Port:

Switch Name / Port:

Cable Type:

Cable Length:

Connector Type:

Fibre Type / Transceiver, if applicable:

Alarm / Symptom:

Fault Start Time:

Fault Frequency:

Operating Condition:

Link LED Status:

Port Speed / Status:

Recent Maintenance:

Cable Inspection:

Connector Inspection:

Routing / EMI Observation:

Cable Test Result:

Optical Power / Fibre Test, if applicable:

Known-Good Substitution Result:

Confirmed Root Cause:

Corrective Action:

Component Replaced:

Post-Repair Link Status:

Communication Verification:

Machine Cycle Verification:

Preventive Action:

Technician:

Work Order:

Date:

## 17. Interview Questions and Answers

### Q1. What is the physical layer in industrial networking?

It is the layer responsible for transmitting raw bits over a physical medium, including copper conductors, optical fibre, connectors, and electrical or optical signalling interfaces.

### Q2. Why can a cable pass a continuity test but still fail Ethernet communication?

Continuity testing verifies conductor connections but does not fully evaluate signal integrity, insertion loss, return loss, crosstalk, or high-frequency transmission performance.

### Q3. What is the difference between single-mode and multimode fibre?

Single-mode fibre supports one principal spatial propagation mode and is commonly used for longer-distance links. Multimode fibre supports multiple modes and is commonly used for shorter-distance links. The compatible transceiver and fibre specifications determine actual performance.

### Q4. What is the difference between D-coded and X-coded M12 Ethernet connectors?

D-coded connectors are commonly used for 10/100 Mbit/s Industrial Ethernet. X-coded connectors support higher-speed Ethernet applications, including 10 Gbit/s when the entire link is compliant.

### Q5. Why does industrial Ethernet fail when a VFD operates?

Electromagnetic interference, poor routing, inadequate bonding, or improper shield termination can affect the physical communication path.

### Q6. What does a link LED indicate?

It generally indicates that a physical link has been established. Activity LEDs may indicate traffic. Exact meanings depend on the equipment manufacturer, and a link light alone does not prove error-free communication.

### Q7. What is an OTDR?

An Optical Time-Domain Reflectometer sends optical test pulses into a fibre and analyzes returned light to characterize events such as breaks, reflections, and loss points.

### Q8. What is the first step when a network link goes down?

Record the affected device and alarm, then check the physical port status, cable seating, connector condition, and compatibility before making configuration changes.

### Q9. Why is cable bend radius important?

Excessive bending can damage the cable structure or increase transmission loss. Fibre is especially sensitive to bending-related attenuation, while copper cable performance can also be affected by deformation.

### Q10. How do you diagnose an intermittent cable fault?

Correlate the fault with movement and machine operation, inspect likely strain points, check port events, and test the cable using an appropriate instrument. Replace components only after gathering evidence.

## 18. Completion Checklist

Understand the OSI physical layer and its role in industrial communication.

Identify copper Ethernet cable categories and industrial cable constructions.

Understand T568A and T568B wiring arrangements.

Inspect RJ45 and M12 connectors.

Recognize EMI-related symptoms and routing problems.

Distinguish single-mode and multimode fibre.

Understand fibre connectors, transceivers, and compatibility.

Apply fibre inspection and handling safety.

Select the correct cable-testing instrument.

Diagnose permanent and intermittent link failures systematically.

Record root cause, corrective action, and post-repair verification.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\19_Breakdown\06_Network_Fault\02_Link - Link: Link lights, speed, duplex