# Network Fault: Device Health and Device Name

Study path: 02_PLAN_WISE_2026\02_INDUSTRY3_0\19_Breakdown\06_Network_Fault\06_Device

## 1. Purpose of Device-Level Network Troubleshooting

A network device can have a healthy Ethernet link, a valid IP address, and a correctly configured protocol while still failing to communicate because the device itself is unhealthy, incorrectly identified, overloaded, restarting, or operating with incompatible configuration.

Device-level troubleshooting examines the condition and identity of the endpoint, including PLCs, remote I/O adapters, HMIs, CNC controllers, robot controllers, VFD communication modules, industrial PCs, gateways, and managed switches.

Typical symptoms include:

A device is unreachable even though its switch port shows an active link.

A PLC or HMI repeatedly disconnects and reconnects.

A device responds slowly or stops updating its data.

A replacement device does not appear under the expected name.

A device has an unexpected IP address or MAC address.

A controller reports a module, interface, or communication fault.

A device reboots intermittently.

Communication fails after firmware or configuration changes.

The device appears online but provides stale, invalid, or inconsistent data.

Engineering software discovers an unexpected device or cannot identify the intended one.

Main objective: Establish whether the endpoint is correctly identified, powered, operating normally, configured correctly, and capable of maintaining the required communication.

## 2. Device-Level Troubleshooting in the Network Stack

Physical Connection

Cable / Connector / Port

↓

Network Configuration

IP / Subnet / VLAN / Routing

↓

Protocol Configuration

Connection / Endpoint / Data Mapping

↓

Device Health

Power / CPU / Memory / Temperature / Diagnostics

↓

Device Identity

Name / MAC / IP / Model / Firmware

↓

Application Behaviour

Valid Data / Updating Values / Correct Function

This is a diagnostic grouping, not a strict protocol sequence. Device health and identity can affect several layers simultaneously.

## 3. Device Identity: What Must Be Verified?

A device may have several identifiers. They serve different purposes and should not be treated as interchangeable.

| Identifier | Meaning | Typical use |
| --- | --- | --- |
| Device name | Human-readable or protocol-specific configured name | Identification in engineering software and device discovery |
| IP address | Logical network-layer address | IP communication |
| MAC address | Link-layer address associated with a network interface | Ethernet identification and switch diagnostics |
| Hostname | Name used by supported network services and operating systems | Name resolution and administration |
| Vendor ID | Manufacturer identifier in supported industrial protocols | Device identification and compatibility |
| Product code | Identifies a device model or product family in supported protocols | Configuration and device recognition |
| Serial number | Unique manufacturer-assigned equipment identifier | Asset tracking and replacement verification |
| Firmware version | Installed device software version | Compatibility and fault investigation |
| Hardware revision | Hardware design or revision identifier | Replacement and compatibility checks |
| Station or node address | Address used by a particular fieldbus | Device identification on that network |
| PROFINET device name | Configured name used for PROFINET device assignment and identification | Controller-device relationship |
| EtherNet/IP identity | Protocol identity information such as vendor, device type, product code, and revision | Device recognition and configuration checks |

The exact fields available depend on the device and protocol.

### 3.1 Why device identity matters

Suppose two controllers have similar names, or a replacement PLC is configured with an old IP address. An engineer may connect successfully to the wrong controller and read or change the wrong configuration.

Before modifying a production device, verify at least:

Physical machine or panel location.

Manufacturer and model.

Serial number or another reliable equipment identifier.

Network interface and MAC address.

Actual IP address and device name.

Expected controller or device role.

Relevant firmware and hardware revision.

Never identify a production controller by IP address alone. Addresses can be changed, reused, duplicated, or assigned to a replacement device.

## 4. Device Name, Hostname and Protocol Name

These names may look similar in software, but they are not necessarily the same configuration item.

### 4.1 Hostname

A hostname identifies a host within supported naming systems. Depending on the environment, it may be resolved through DNS, local name resolution, or another configured mechanism.

Example:

PLC-LINE01

A hostname may be used for administration or application connections, but an industrial application may still connect directly to a configured IP address.

### 4.2 PROFINET device name

PROFINET uses a configured device name to identify and assign a device within the automation network. The controller's expected configuration must correspond to the actual device configuration.

Common faults include:

Device name is missing.

Device name does not match the engineering configuration.

A replacement device has a default name.

Two devices have conflicting names.

The wrong physical device receives the name assignment.

A device may have correct IP settings yet fail to establish the intended PROFINET relationship if the device name or configuration is incorrect.

### 4.3 EtherNet/IP identity

EtherNet/IP devices expose identity information defined by the protocol, such as vendor, device type, product code, revision, and device status.

The controller may compare the configured device identity with the detected identity. Depending on the controller and configuration, a mismatch may generate a warning or prevent the expected connection.

### 4.4 Name and identity verification

1.	Read the actual name and identity from the device using an approved diagnostic method.

2.	Compare them with the engineering project's expected configuration.

3.	Confirm that the physical device corresponds to the intended machine or network location.

4.	Check for duplicate names or addresses where uniqueness is required.

5.	Correct the mismatch using the manufacturer's supported procedure.

6.	Confirm that the controller or engineering software identifies the correct device.

Do not rename a production device simply because its current name looks untidy. First establish whether the name is part of a protocol assignment, project configuration, or other machine dependency.

## 5. Device Health Parameters

Device health is broader than whether the power LED is on. A device may remain powered while its CPU, communication interface, internal temperature, storage, or firmware encounters a fault.

| Health parameter | What it indicates | Potential symptom |
| --- | --- | --- |
| Power status | Whether the device has an acceptable power supply | Shutdowns, restarts, loss of communication |
| CPU load | Processing demand | Delayed responses or missed deadlines |
| Memory usage | Available operating memory | Application faults or resource exhaustion |
| Temperature | Internal thermal condition | Reduced reliability, alarms, or shutdown |
| Supply voltage | Electrical input condition | Resets, unstable interfaces, or faults |
| Communication status | State of network or protocol interfaces | Connection loss or stale data |
| Watchdog status | Whether execution or communication deadlines are being met | Controller fault, task restart, or timeout |
| Storage health | Condition of supported storage devices | Logging failures, slow operation, or startup problems |
| Firmware status | Installed software revision and reported condition | Compatibility problems or known defects |
| Module status | Health of installed modules or interfaces | Missing I/O, interface errors, or degraded operation |
| Error log | Recorded device events and diagnostic codes | Evidence of intermittent or recurring faults |
| Uptime and restart history | Operating duration and restart events | Unexpected reboot or power interruption |
| Link and packet statistics | Communication activity and errors | Intermittent communication or degraded performance |

Not every device exposes all these parameters. Use only diagnostics supported by the particular product.

## 6. Power and Restart Problems

Unexpected restarts can create symptoms that look like network or protocol faults.

### 6.1 Common causes

Unstable 24 V DC supply.

Loose or damaged power wiring.

Voltage dips during machine operation.

Failed power supply or redundant power input.

Overtemperature.

Internal hardware failure.

Watchdog-triggered restart.

Firmware or application crash.

Deliberate restart during maintenance.

Brownout during a supply interruption.

### 6.2 Diagnostic procedure

1.	Record the exact time of the communication failure.

2.	Check the device's power and diagnostic indicators.

3.	Inspect restart history or event logs if available.

4.	Verify supply voltage using the approved electrical procedure.

5.	Compare restart timestamps with switch link-down events and controller alarms.

6.	Check temperature, ventilation, and loading where applicable.

7.	Determine whether the device rebooted or only its network interface disconnected.

8.	Correct the confirmed cause and verify stable operation.

### 6.3 Correlating restart and network events

If a switch log shows a port going down at the same time a PLC records a restart, the PLC restart may explain the network interruption.

However, matching timestamps alone do not prove causation. A power fault, switch problem, or common upstream event could affect both devices.

Collect evidence from more than one source where practical.

## 7. Device Status LEDs and Diagnostic Indicators

LED meanings vary by manufacturer and model. Use the relevant manual and diagnostic reference.

| Indicator | Possible meaning | Recommended check |
| --- | --- | --- |
| Power LED off | Missing supply or internal power fault | Check approved supply circuit and device condition |
| Run or status LED normal | Device may be in its expected operating state | Verify diagnostics and actual function as well |
| Fault LED on | Device or application fault | Read diagnostic code or fault log |
| Network LED off | No link or interface inactive | Check cable, switch port, and interface configuration |
| Network LED flashing | Activity or another model-specific state | Confirm the manufacturer's LED definition |
| I/O status LED fault | I/O connection or module problem | Inspect module diagnostics and controller configuration |
| Temperature alarm | Device exceeds an acceptable thermal condition | Inspect ambient temperature, ventilation, and load |
| System LED cycling during startup | Boot or initialization activity on some models | Check whether startup completes normally |

Do not infer a specific fault from a flashing pattern without verifying the device's LED code table.

## 8. Firmware and Hardware Compatibility

Firmware controls the behaviour of a device's internal software. A firmware revision may add features, change behaviour, fix defects, or affect compatibility with other components.

### 8.1 Common compatibility problems

Controller project created for a different device revision.

Replacement module uses a different hardware revision.

Protocol features differ between firmware versions.

Engineering software does not support the installed firmware.

A device firmware upgrade changes configuration requirements.

Firmware and device description files are inconsistent.

A replacement device does not support a required option or communication mode.

### 8.2 Diagnostic procedure

1.	Record the device model, hardware revision, and firmware version.

2.	Compare the installed version with the approved machine documentation.

3.	Review controller or engineering software diagnostics.

4.	Check manufacturer compatibility documentation.

5.	Confirm required options and protocol features.

6.	Determine whether the issue began after a firmware or hardware change.

7.	Apply an approved version or configuration only after reviewing the impact and recovery procedure.

Production caution: Firmware changes can interrupt communication, invalidate compatibility assumptions, or require a controller restart. Do not update firmware merely because a newer version exists.

## 9. Device Resource Limits and Performance

Some devices have limits on communication connections, simultaneous clients, cyclic I/O connections, active sessions, request rates, memory, or processing capacity.

A device may function normally at low load but become slow or unreliable when too many clients access it.

### 9.1 Common symptoms

Intermittent request timeouts.

Slow engineering software response.

SCADA tags update less frequently than expected.

New connections are rejected.

Device response deteriorates when multiple clients connect.

Communication becomes unstable during high activity.

CPU or memory usage increases sharply.

### 9.2 Diagnostic checks

Review available CPU, memory, and connection statistics.

Check configured and active connection counts.

Identify engineering PCs, HMI panels, SCADA servers, and gateways accessing the device.

Review polling frequency and request grouping.

Inspect diagnostic logs for rejected connections or resource warnings.

Compare the observed load with manufacturer limits.

Check whether an unintended client or repeated reconnect loop is consuming resources.

Do not assume that adding another HMI or SCADA client has no impact. Some devices have strict connection limits or recommend a particular data-sharing architecture.

## 10. Network Interface Health

A device can be healthy overall while one Ethernet interface, module, or communication channel is faulty.

### Possible symptoms

One network port works while another does not.

The device communicates through an alternate interface but not the intended one.

Link status is unstable despite a known-good cable.

Error counters increase on one interface.

The wrong interface is used for engineering or production communication.

Interface configuration differs from the approved design.

### Diagnostic method

1.	Identify the intended network interface.

2.	Confirm its MAC address and IP configuration.

3.	Check interface status and error counters.

4.	Verify the connected switch port and cable.

5.	Inspect whether the interface is enabled and configured for the intended function.

6.	Check routing or interface-selection settings on multi-interface devices.

7.	Compare with another supported interface only if the network design and safety requirements permit it.

A multi-port device may use separate interfaces for distinct networks. Never connect interfaces together or bridge them casually. Doing so may create loops, unintended routing, or loss of network segmentation.

## 11. Device Discovery and Identification Tools

Different vendors provide different tools for discovering devices, assigning names, or displaying identity information.

Examples include:

Manufacturer-specific PLC discovery and configuration utilities.

PROFINET discovery and device-name assignment tools.

EtherNet/IP browsing and device identity diagnostics.

Managed switch MAC address tables.

Windows network configuration tools.

Device web interfaces where supported.

Controller hardware diagnostics.

Engineering software online comparison and device status views.

Use approved tools and confirm that the discovery method is compatible with the device and network.

### 11.1 Windows diagnostics

Display network interface configuration:

ipconfig /all

Display the ARP cache:

arp -a

Test IP reachability:

ping 192.168.10.10

Resolve a hostname using the configured Windows name-resolution mechanisms:

nslookup PLC-LINE01

Inspect a route to a target:

tracert 192.168.20.50

Replace example values with the approved device name or address.

These commands have limitations. For example, nslookup primarily queries DNS and may not reflect all local hostname-resolution mechanisms. A successful ping also does not prove that the intended physical device answered if the IP address is duplicated.

## 12. Device Replacement and Configuration Recovery

Replacing a failed industrial device involves more than connecting a new unit. The replacement must be identified correctly and configured to match the machine's approved design.

### 12.1 Before replacement

Record the original model and hardware revision.

Record the serial number and firmware version.

Capture the IP address, subnet mask, and gateway where applicable.

Record the device name and MAC address.

Save approved configuration backups.

Record relevant protocol and application settings.

Document the connected ports and network topology.

Identify dependencies such as PLC projects, HMI tags, SCADA endpoints, or remote I/O mappings.

### 12.2 After replacement

1.	Confirm the replacement model and supported features.

2.	Verify the correct firmware and hardware compatibility.

3.	Restore or configure the approved settings.

4.	Assign the correct name and network configuration.

5.	Confirm that the address is not already in use.

6.	Verify the intended switch port and VLAN.

7.	Check protocol connection and device diagnostics.

8.	Validate data mapping and application operation.

9.	Confirm the actual machine function.

10.	Update asset records and the device register.

### 12.3 MAC address changes

A replacement device normally has a different physical MAC address from the original device. This is expected unless a supported mechanism explicitly allows an address to be preserved or overridden.

A different MAC address does not automatically indicate a fault. However, switch security rules, address reservations, or external management systems may depend on the device's identity and require approved updates.

Do not copy or spoof another device's MAC address unless the manufacturer and network design explicitly support that method and the change is authorized.

## 13. Device Health Versus Network Health

A key troubleshooting skill is distinguishing an endpoint fault from a network fault.

| Observation | Possible interpretation | Next diagnostic step |
| --- | --- | --- |
| Device power LED is off | Power supply or hardware problem | Verify approved supply and device status |
| Device is powered, but link LED is off | Interface, cable, or switch-port issue | Check both ends of the connection |
| Link is active, but device is unreachable | IP, VLAN, interface, or device problem | Verify addressing and endpoint configuration |
| Ping works, but protocol fails | Service, protocol configuration, permissions, or resource problem | Inspect protocol diagnostics |
| Protocol is connected, but values are wrong | Mapping, data type, scaling, or application logic | Compare source data and mapped values |
| Device restarts repeatedly | Power, thermal, watchdog, firmware, or hardware issue | Correlate restart history with electrical and diagnostic evidence |
| Only one interface fails | Interface-specific configuration or hardware fault | Compare interface settings and port diagnostics |
| Several devices fail simultaneously | Shared power, switch, uplink, or network problem | Identify the common infrastructure |
| Device identity differs from records | Replacement, misconfiguration, or duplicate identity | Verify physical identity and approved device records |

## 14. Practical Industrial Breakdown Scenarios

### Scenario 1: PLC responds to ping but controller communication fails

Observed condition: The PLC is reachable by IP, but the engineering software reports that the controller is unavailable.

Investigation:

1.	Verify the PLC model and actual device identity.

2.	Check the selected engineering interface and target address.

3.	Confirm that the required service is enabled and accessible.

4.	Inspect the controller's diagnostic status.

5.	Verify firmware and engineering software compatibility.

6.	Check connection limits and access permissions.

7.	Review the switch and protocol logs if the fault persists.

Possible root causes: Wrong target device, incompatible firmware, unavailable service, access restriction, or exhausted connection resources.

Verification: Confirm that the engineering software connects to the intended PLC and displays the correct controller identity.

### Scenario 2: Replacement device does not establish communication

Observed condition: A replacement remote I/O adapter is powered and connected, but the PLC reports an I/O connection fault.

Investigation:

1.	Verify the replacement model and revision.

2.	Check its configured IP address and device name.

3.	Confirm that the address is not duplicated.

4.	Compare its protocol identity with the controller's configuration.

5.	Verify the module layout and connection parameters.

6.	Check firmware compatibility and device diagnostics.

7.	Confirm switch-port and VLAN configuration.

Possible root causes: Incorrect device name, incompatible revision, wrong connection parameters, or an unapproved replacement model.

Verification: Confirm that the PLC establishes the intended connection and all expected I/O data updates correctly.

### Scenario 3: HMI communication drops when the machine becomes busy

Observed condition: The HMI works normally during idle periods but displays communication errors during production.

Investigation:

1.	Check HMI and PLC event logs at the fault time.

2.	Inspect PLC resource usage and active connections where available.

3.	Review HMI polling rates and tag configuration.

4.	Check switch errors and network traffic.

5.	Verify device temperature and supply stability.

6.	Determine whether another client is generating excessive requests.

7.	Compare actual performance with manufacturer recommendations.

Possible root causes: Resource limitations, excessive polling, intermittent network faults, or unstable device power.

Verification: Confirm stable data updates during representative production load.

### Scenario 4: Engineering software connects to the wrong controller

Observed condition: The engineering software connects successfully, but the displayed project or controller identity does not match the intended machine.

Investigation:

1.	Verify the physical machine and controller location.

2.	Read the connected device's IP address and MAC address.

3.	Compare its model, serial number, and identity with the equipment register.

4.	Check for duplicate IP addresses or reused network settings.

5.	Confirm the intended engineering project and controller target.

6.	Stop before downloading or modifying any program until identity is confirmed.

Possible root causes: Duplicate IP address, incorrect device selection, stale engineering configuration, or an incorrectly configured replacement.

Verification: Confirm the connected controller's identity and machine assignment before making any changes.

### Scenario 5: Device repeatedly restarts and disappears from the network

Observed condition: The switch logs repeated link-down events, and the device intermittently becomes unreachable.

Investigation:

1.	Correlate the switch event timestamps with the device's restart history.

2.	Check the power supply and approved voltage measurements.

3.	Inspect connectors and terminals for looseness or damage.

4.	Review thermal alarms and cabinet conditions.

5.	Check watchdog, firmware, and hardware diagnostics.

6.	Determine whether the interface resets independently of the main device.

7.	Correct the confirmed power, thermal, configuration, or hardware fault.

Possible root causes: Unstable supply, device reboot, overheating, failing interface, or internal hardware failure.

Verification: Confirm stable device operation, uninterrupted link status, and normal protocol communication.

## 15. Preventive Maintenance Checklist

### Device identity and records

Maintain a device register containing name, model, serial number, IP address, MAC address, and location.

Record firmware and hardware revisions where relevant.

Maintain approved device configuration backups.

Document protocol roles, communication endpoints, and dependencies.

Verify replacement-device identity before commissioning.

Check for duplicate names or addresses where uniqueness is required.

### Device health

Check power, system, and fault indicators.

Review available diagnostic logs and restart history.

Investigate recurring communication losses.

Check temperature and ventilation where applicable.

Review CPU, memory, connection count, or storage health where available.

Inspect network-interface status and error counters.

Verify that firmware and configuration match the approved design.

### Operational verification

Confirm the intended device is being accessed.

Verify the network and protocol connection states.

Check data freshness and application values.

Validate normal machine operation after maintenance.

Document configuration changes and corrective actions.

## 16. Device Breakdown Record Template

Machine / Line:

Device Name:

Device Role:

Manufacturer:

Model:

Serial Number:

Hardware Revision:

Firmware Version:

Physical Location:

MAC Address:

IP Address:

Subnet Mask:

Default Gateway:

Hostname / Protocol Name:

Network Interface:

Switch / Port:

VLAN, if applicable:

Power Status:

Supply Voltage:

System Status:

Temperature / Alarm:

CPU / Memory Status:

Restart History:

Interface Error Counters:

Protocol Connection Status:

Active Connection Count:

Device Diagnostic Code:

Exact Error Text:

Fault Timestamp:

Expected Device Identity:

Actual Device Identity:

Configuration Before Repair:

Configuration After Repair:

Confirmed Root Cause:

Corrective Action:

Component Replaced:

Device Identity Verified:

Network Communication Verified:

Protocol Communication Verified:

Data Mapping Verified:

Machine Function Verified:

Technician:

Work Order:

Date:

## 17. Interview Questions and Answers

### Q1. Why is device identity important during troubleshooting?

Correct identification prevents an engineer from diagnosing or modifying the wrong controller, particularly when addresses are duplicated, reused, or changed after replacement.

### Q2. What is the difference between a hostname and an IP address?

A hostname is a name used by supported naming and resolution mechanisms. An IP address is the logical address used for IP communication.

### Q3. What is a PROFINET device name used for?

It identifies a device in PROFINET configuration and helps establish the intended relationship between the controller and the field device.

### Q4. Why can a powered device still be unhealthy?

It may have a CPU, memory, temperature, firmware, communication-interface, watchdog, or internal hardware fault despite receiving power.

### Q5. Why should a replacement device's firmware be checked?

Firmware can affect supported features, compatibility, communication behaviour, and configuration requirements.

### Q6. What could cause repeated device restarts?

Possible causes include unstable power, overheating, watchdog events, application crashes, firmware defects, or failing hardware.

### Q7. Why can communication fail when too many clients connect?

Some devices have limits on simultaneous sessions, cyclic connections, processing capacity, or request rate. Exceeding these limits can cause delays or rejected connections.

### Q8. What is the difference between device health and network health?

Device health concerns the endpoint's operating condition. Network health concerns the communication infrastructure and path. A fault in either can interrupt communication.

### Q9. Why is a changed MAC address after replacement not necessarily a fault?

The replacement device normally has its own MAC address. However, switch security rules or address-management systems may need approved updates to recognize the replacement.

### Q10. What should be verified before downloading a PLC program?

Confirm the physical controller identity, machine assignment, project target, controller revision, and approved backup. A successful connection alone does not prove that the correct controller is selected.

### Q11. How can an engineer determine whether a device reboot caused a network outage?

Correlate the device's restart history with switch link events, controller diagnostics, and other timestamped logs. Matching evidence supports the diagnosis, but the root cause still needs confirmation.

### Q12. What must be checked after restoring a device?

Verify identity, configuration, network connectivity, protocol communication, data correctness, diagnostic status, and actual machine function.

## 18. Completion Checklist

Distinguish device identity from IP address and MAC address.

Understand hostname and protocol-specific device names.

Verify model, serial number, firmware, and hardware revision.

Interpret device status indicators using the correct manual.

Diagnose power interruptions and unexpected restarts.

Recognize resource, temperature, and interface-health problems.

Understand device and protocol compatibility.

Use appropriate device-discovery and diagnostic tools.

Verify replacement configuration and address uniqueness.

Correlate device logs with network events.

Separate endpoint faults from shared network faults.

Validate the intended application and machine function after repair.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\19_Breakdown\06_Network_Fault\07_App - Application: PLC/SCADA data and logic