# End-of-Life Management in Industrial Automation

## 1. Definition and Purpose

End-of-life (EOL) is a lifecycle stage or milestone at which a product, system, or service reaches a defined endpoint established by its manufacturer, supplier, or operating organization.

In industrial automation, EOL may apply to a PLC CPU, I/O module, HMI, VFD, servo drive, CNC controller, robot controller, industrial PC, network switch, sensor, safety device, engineering software, or complete machine.

EOL management is the process of identifying affected equipment, assessing the consequences, securing recovery options, and planning repair, replacement, migration, or decommissioning.

Important distinction: EOL does not always mean that equipment must immediately stop operating. The manufacturer may stop selling a product while continuing repairs or technical support for a defined period. Always check the specific product notice because manufacturers do not use lifecycle terms identically.

## 2. Why EOL Management Matters

Industrial automation equipment can remain operational for decades, even when its electronic components, software, and support services are no longer available.

EOL management helps organizations:

Prevent prolonged downtime caused by unavailable components.

Identify lifecycle risks before a failure occurs.

Plan replacements within production shutdown windows.

Preserve PLC programs, CNC parameters, robot programs, and engineering software.

Establish realistic spare-part quantities.

Identify approved successor products.

Control migration and commissioning costs.

Maintain machine safety and process quality.

Reduce cybersecurity exposure from unsupported products.

Coordinate procurement, maintenance, engineering, IT/OT, production, and finance.

The central objective is to avoid discovering that a critical component is no longer obtainable at the exact moment it fails. Industrial equipment has a talent for choosing inconvenient moments.

## 3. EOL Terminology

| Term | Meaning | Typical action |
| --- | --- | --- |
| End of sale | New sales stop or are restricted | Review purchasing options and successors |
| End of manufacturing | Original product production ends | Assess stock and replenishment risk |
| End of support | Specified support services end | Assess repair, software, and technical risks |
| End of maintenance | Maintenance services or updates end under the stated policy | Plan alternative support or migration |
| End of repair | Manufacturer repair service ends | Identify specialist repair or replacement options |
| End of security updates | Security patches stop | Assess exposure and compensating controls |
| End of life | Product reaches a manufacturer-defined lifecycle endpoint | Follow the product-specific EOL notice |
| Last-time buy | Final ordering opportunity before normal supply ends | Calculate justified purchase quantities |
| Successor product | Product designated to replace the original model | Validate technical and application compatibility |
| Decommissioning | Equipment is formally removed from service | Isolate, document, dispose of, and close records |

These milestones may occur on different dates. An EOL notice must therefore be reviewed for its exact scope, conditions, and deadlines.

## 4. Typical EOL Timeline

Product in Active Sales

↓

Product Becomes Mature

↓

End-of-Sale Announcement

↓

Last-Time-Buy Period, If Offered

↓

End of Manufacturing

↓

Spare Parts and Repair Support Continue, If Available

↓

Support Services End

↓

Product Reaches Its Defined EOL Milestone

↓

Migration, Replacement, Controlled Retention, or Decommissioning

This is an illustrative sequence, not a universal manufacturer policy. Some products skip stages, combine milestones, or continue selected services after others have ended.

## 5. EOL Versus Obsolescence Versus Legacy

| Concept | Main meaning | Example |
| --- | --- | --- |
| EOL | A defined lifecycle endpoint or milestone | A manufacturer announces the end of support for a PLC family |
| Obsolescence | Practical difficulty or inability to obtain or support a product | A discontinued board cannot be sourced or repaired economically |
| Legacy system | An older system that remains in operation | An older test bench still running its original PLC |
| Unsupported system | Required support or updates are unavailable | An industrial PC operating without security updates |
| End of sale | New commercial sales have stopped | A VFD is no longer available for normal new-product orders |

A legacy machine can still be supported. An EOL product may continue to operate. An obsolete component may exist in a machine that is otherwise modern. These distinctions matter when prioritizing actions.

## 6. Identifying EOL Equipment

A reliable EOL assessment begins with accurate identification of installed products.

### 6.1 Information to Collect

Manufacturer and complete model number.

Product family and hardware revision.

Serial number and manufacturing date, where relevant.

Firmware version.

Engineering software and runtime versions.

Installed accessories and communication modules.

Machine and panel identification.

Current spare stock and repair options.

Operational criticality and failure history.

### 6.2 Verification Sources

Use the following sources in order of preference:

1.	Official manufacturer product lifecycle portal.

2.	Product-specific EOL or discontinuation notice.

3.	Official successor-product and migration documentation.

4.	Manufacturer repair and support policy.

5.	Authorized distributor confirmation where information is incomplete.

Record the source, publication date, applicable model variants, and the date on which the lifecycle information was checked.

Do not infer that a product is EOL merely because it is old or absent from a distributor's website.

## 7. EOL Management for Major Automation Components

### 7.1 PLC CPU and I/O

Potential consequences include unavailable CPUs, communication modules, I/O cards, memory devices, and engineering software.

Required actions:

Preserve the PLC source project and available controller upload.

Record CPU, I/O, firmware, and communication configurations.

Confirm the availability of spare CPUs and modules.

Check program conversion and hardware compatibility.

Identify the proposed successor platform.

Validate I/O mapping, instructions, communications, and scan behavior.

Prepare a migration and rollback plan.

A replacement CPU may require program conversion, changes to hardware configuration, or redesign of communication interfaces.

### 7.2 HMI and SCADA

Potential EOL issues include discontinued panels, old runtime software, unsupported operating systems, and incompatible communication drivers.

Required actions:

Preserve development projects and runtime configuration.

Record software versions, licenses, and dependencies.

Document PLC tags, alarms, recipes, and trends.

Check historical data and database integration.

Verify display, touch, communication, and operator workflow compatibility.

Validate alarm behavior and operator access after migration.

### 7.3 VFD and Servo Drive

Potential issues include unavailable drives, discontinued option cards, obsolete feedback interfaces, and incompatible parameter structures.

Required actions:

Back up parameters and record motor nameplate data.

Record control mode, fieldbus, I/O, and braking configuration.

Verify the replacement's voltage, current, overload, and duty ratings.

Confirm motor and encoder compatibility.

Check fault handling and interlocking.

Test acceleration, deceleration, stopping, and restart behavior.

### 7.4 CNC and Robot Controllers

EOL can affect controller boards, servo systems, teach pendants, memory devices, proprietary software, and service tools.

Preserve:

CNC programs, parameters, offsets, and compensation data.

Robot programs, mastering data, calibration information, and tool/work frames.

Machine-builder-specific configuration.

Safety configuration and validation records.

Required software, licenses, and restore procedures.

Migration must be validated against the complete machine process, not merely the controller's ability to power up.

### 7.5 Industrial PCs and Network Devices

EOL industrial PCs can depend on unsupported operating systems, proprietary expansion cards, old drivers, and application licenses. Older network devices may have limited security features or unavailable replacement hardware.

Required actions include preserving approved system images and configurations, documenting network dependencies, confirming replacement compatibility, and planning cybersecurity controls.

## 8. EOL Risk Assessment

EOL status alone does not determine the urgency of replacement. Risk depends on the consequences of failure and the organization's ability to recover.

Assess:

Equipment criticality.

Failure history and condition.

Spare availability and supplier lead time.

Repair capability and turnaround time.

Production downtime consequence.

Software and backup availability.

Cybersecurity exposure.

Safety and regulatory implications.

Successor compatibility.

Migration complexity and shutdown requirements.

### 8.1 Example Prioritization Matrix

| Lifecycle condition | Criticality | Recovery capability | Typical priority |
| --- | --- | --- | --- |
| EOL announced | Low | Strong | Planned review |
| EOL announced | Medium | Moderate | Schedule mitigation |
| Unsupported | High | Limited | High-priority action |
| EOL and no spares | High | Poor | Urgent contingency and migration planning |
| Unsupported safety-related component | Safety-critical | Uncertain | Immediate engineering and safety assessment |

This is a planning aid, not a substitute for a formal risk assessment. A safety-related or actively exploited cybersecurity weakness can require urgent action even if spare parts are available.

## 9. EOL Register

Maintain a controlled register that links lifecycle data to actual installed equipment.

| Field | Purpose |
| --- | --- |
| Asset ID | Unique installed equipment reference |
| Machine or line | Identifies the production location |
| Manufacturer | Identifies the supplier |
| Exact model | Supports accurate lifecycle verification |
| Hardware revision | Distinguishes product variants |
| Firmware or software version | Establishes configuration requirements |
| EOL status | Records the verified lifecycle milestone |
| Notice date | Records when the announcement was published |
| End-of-sale date | Records the applicable sales deadline |
| End-of-manufacturing date | Records the production deadline |
| End-of-support date | Records the applicable support deadline |
| Repair status | Records available repair services |
| Successor model | Identifies a potential replacement |
| Compatibility result | Records engineering validation |
| Spare quantity | Records available usable stock |
| Lead time | Supports recovery planning |
| Risk rating | Prioritizes action |
| Action owner | Assigns responsibility |
| Target date | Controls completion |
| Evidence location | Stores lifecycle notices and technical records |

Use a separate value for unknown or unconfirmed dates. An empty field must not be interpreted as evidence that support continues indefinitely.

## 10. EOL Response Strategies

### 10.1 Continue Operating Under Controlled Conditions

Suitable when the system remains functional and the assessed risks are acceptable.

Required controls may include verified backups, sufficient recovery arrangements, periodic inspections, approved network restrictions, and a documented migration plan.

### 10.2 Repair and Refurbish

Suitable when specialist repair is available and the repaired unit can be tested adequately.

Check repair quality, replaced components, warranty, turnaround time, and whether the repair restores the reliability required for the application.

### 10.3 Purchase Strategic Spares

Suitable when the component is critical, replacement is difficult, and the equipment will remain in service for a defined period.

Stock quantity must account for failure probability, lead time, repair returns, storage conditions, and the planned migration date.

### 10.4 Retrofit a Subsystem

Replace a specific component while retaining the rest of the machine.

Examples include replacing an obsolete HMI, VFD, communication gateway, or I/O subsystem.

Verify mechanical fit, electrical interfaces, communication behavior, configuration requirements, and process validation.

### 10.5 Migrate the Control Platform

Replace the legacy controller or control architecture with a supported platform.

This requires program conversion, I/O mapping, communication validation, safety assessment, commissioning, and a rollback strategy.

### 10.6 Decommission the Equipment

Suitable when the machine is no longer needed or the cost and risk of continued operation are unjustifiable.

Decommissioning includes controlled isolation, removal of stored energy, data preservation where required, asset-record updates, and compliant disposal.

## 11. EOL Spare-Part Planning

Spare planning should be linked to installed-base mapping and criticality.

Recommended actions:

Identify every installed component affected by the notice.

Count usable spares across stores, maintenance areas, and approved service channels.

Confirm whether stored units are compatible with installed revisions.

Check storage requirements and shelf-life limits.

Assess repair turnaround and repair success rates.

Identify alternate parts and successor models.

Calculate coverage until planned migration.

Assign procurement and engineering approval responsibilities.

Avoid treating every EOL component as equally critical. A common sensor with an approved equivalent and a discontinued proprietary CNC control board require very different strategies.

## 12. Last-Time-Buy Planning

A last-time buy is a purchasing action that may be available before the manufacturer closes normal ordering. It is not mandatory for every EOL product.

Before ordering, evaluate:

Forecast consumption and failure rates.

Current usable stock.

Expected remaining service life.

Supplier and manufacturer deadlines.

Storage degradation and warranty restrictions.

Repair and refurbishment options.

Successor-product availability.

Migration budget and schedule.

Risk of unused stock after modernization.

A simple coverage estimate is:

Q=max(0,D×T−S)

Where:

Q is the estimated additional quantity.

D is expected annual consumption.

T is the required coverage period in years.

S is the usable stock already available.

For example, if expected consumption is 1.5 units per year, the required coverage is 4 years, and 2 usable units are already in stock:

Q=max(0,1.5×4−2)=4

This estimates 4 additional units before adjustment for uncertainty, repair returns, storage life, and migration timing. The formula is a starting point, not permission to spend the budget on electronics that may outlive the machine.

## 13. EOL and Cybersecurity

EOL can increase cybersecurity risk when software updates, security patches, or vendor assistance are no longer available.

Potential risks include:

Unpatched firmware vulnerabilities.

Unsupported operating systems.

Outdated communication services.

Weak authentication or encryption.

Incompatible modern security tools.

Limited incident-response support.

Possible controls include network segmentation, restricted remote access, approved engineering workstations, secure backups, controlled data pathways, and monitoring.

These measures reduce exposure but may not eliminate it. If residual risk remains unacceptable, migration or decommissioning may be necessary.

## 14. EOL Migration Planning

A migration project should be defined before the existing system becomes impossible to recover.

Confirm EOL Notice and Installed Assets

↓

Assess Criticality and Recovery Risk

↓

Preserve Programs, Parameters, and Backups

↓

Identify Successor and Technical Dependencies

↓

Compare Repair, Retrofit, and Migration Options

↓

Approve Budget, Scope, and Shutdown Window

↓

Engineer and Test the Replacement

↓

Validate Safety, Quality, and Production Functions

↓

Commission and Verify Recovery Procedures

↓

Update Documentation and Close EOL Actions

### 14.1 Migration Acceptance Criteria

Before releasing the machine for production, define measurable acceptance criteria for:

I/O operation and communication.

Machine sequence and interlocks.

Alarm handling and fault recovery.

Motion and drive performance.

Quality measurements and test results.

Safety functions and validation.

HMI operation and user access.

Data collection and reporting.

Backup restoration and rollback readiness.

The acceptance criteria should reflect the actual machine and process. A generic checklist cannot validate every automation application.

## 15. Practical Case Study

### Discontinued VFD on a Critical Test Bench

Situation: A test bench uses a discontinued VFD. The drive remains operational, but replacement stock is unavailable from the normal supplier. A compatible successor appears to exist.

Assessment:

Record the exact drive model, rating, firmware, and option cards.

Verify the official EOL notice and support status.

Review the motor nameplate, drive parameters, braking arrangement, and control interfaces.

Confirm the successor's electrical and communication compatibility.

Evaluate repair options and actual turnaround time.

Preserve the existing parameter set and relevant machine documentation.

Prepare a controlled replacement plan and define acceptance tests.

Establish an interim recovery strategy based on the assessed risk.

Expected outcome: The plant has a documented plan for either repair or replacement, with technical compatibility verified before the original drive fails.

## 16. Common EOL Management Mistakes

Assuming all EOL milestones occur on the same date.

Treating EOL status as proof that a product is already defective.

Waiting until failure before checking spare availability.

Purchasing large quantities without a consumption or coverage calculation.

Ignoring software licenses and engineering-tool dependencies.

Assuming successor products are automatically compatible.

Failing to verify backup restoration.

Replacing control hardware without validating machine safety.

Ignoring unsupported operating systems and network exposure.

Failing to assign action owners and deadlines.

Closing an EOL action after purchasing parts without confirming the actual risk has been reduced.

## 17. Interview Questions and Answers

### Q1. What is end-of-life in industrial automation?

EOL is a manufacturer- or organization-defined lifecycle endpoint for a product, system, or service. It may affect sales, manufacturing, repairs, technical support, or software updates.

### Q2. Does EOL mean the equipment must be stopped immediately?

No. Continued operation depends on the applicable lifecycle notice, technical condition, support availability, and assessed safety, cybersecurity, and production risks.

### Q3. What is the difference between end of sale and end of support?

End of sale means normal commercial sales have ended. End of support means specified support services have ended. They can occur at different times.

### Q4. How should a plant manage EOL PLCs?

Verify the exact lifecycle status, preserve and test backups, identify available spares, assess criticality, evaluate successor compatibility, and plan repair or migration.

### Q5. What determines EOL replacement priority?

Equipment criticality, failure consequences, spare availability, repair lead time, cybersecurity exposure, safety implications, and migration feasibility.

### Q6. What is the purpose of an EOL register?

It connects manufacturer lifecycle information to installed assets, spare availability, risk ratings, planned actions, owners, and deadlines.

### Q7. What should be considered before a last-time buy?

Expected consumption, usable stock, coverage period, storage life, repair options, product compatibility, migration schedule, and total lifecycle cost.

### Q8. Why is successor validation necessary?

The replacement may differ in electrical ratings, communication interfaces, firmware, parameter structure, software compatibility, and application behavior.

### Q9. How does EOL affect cybersecurity?

Products may no longer receive security patches or vendor assistance, increasing the difficulty of mitigating vulnerabilities.

### Q10. When should EOL management lead to decommissioning?

When continued operation is no longer required or when the residual technical, safety, cybersecurity, support, or financial risk cannot be acceptably controlled.

## 18. Practical Competency Checklist

Explain EOL, end of sale, end of manufacturing, and end of support.

Verify lifecycle notices for exact models and revisions.

Maintain an installed-equipment EOL register.

Assess production, repair, safety, and cybersecurity risks.

Preserve and verify engineering backups.

Confirm spare availability and supplier lead times.

Calculate justified spare coverage.

Evaluate repair, retrofit, migration, and decommissioning.

Validate successor compatibility before procurement or installation.

Define migration acceptance and rollback criteria.

Assign owners and target dates to lifecycle actions.

Update spare, asset, maintenance, and technical records after closure.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\24_Obsolescence\04_Last_Time_Buy - Last-time buy