# Historical Versions: Parameters

## 1. Purpose and Scope

Parameter version management is the practice of recording, preserving, comparing, validating, and recovering configuration values that determine how an industrial machine or automation device operates.

Parameters are often less visible than PLC programs, but their impact can be just as significant. A machine may have unchanged PLC logic and unchanged firmware yet behave differently because a drive acceleration time, CNC setting, servo gain, vision threshold, communication timeout, or test limit has changed.

The objective is to preserve not only the parameter values, but also their meaning, source, operating context, validation status, and change history.

This topic covers:

Industrial parameter types and classifications.

Parameter backups and historical snapshots.

Machine-specific parameter identification.

Parameter naming, units, ranges, and dependencies.

Before-and-after comparison.

Parameter changes during maintenance and commissioning.

Safe restoration and validation.

Parameter management for PLCs, CNCs, robots, drives, vision systems, and test benches.

Auditability, cybersecurity, and recovery planning.

## 2. What Is a Parameter?

A parameter is a configurable value that influences the behavior, limits, timing, communication, control, or operation of a system.

Examples include:

PLC timer presets.

VFD acceleration and deceleration times.

Servo gain and tuning settings.

CNC axis limits and machine constants.

Robot speed and motion settings.

Vision inspection thresholds.

HMI communication timeouts.

Network communication settings.

Test-bench measurement limits.

Alarm thresholds and process setpoints.

Parameters are not necessarily all stored in one file. They may exist in a device's internal memory, an engineering project, a recipe database, a configuration file, a removable memory card, or an external application.

A complete parameter backup strategy must identify which values exist, where they are stored, and which capture method preserves them correctly.

## 3. Parameter Categories

| Category | Purpose | Industrial examples |
| --- | --- | --- |
| Control parameters | Influence control behavior | PID gains, control modes |
| Timing parameters | Define timing behavior | PLC timer presets, communication timeouts |
| Motion parameters | Define motion characteristics | Speed limits, acceleration, deceleration |
| Drive parameters | Configure motor and drive behavior | Motor ratings, ramp times, control mode |
| CNC parameters | Configure machine operation | Axis settings, machine constants |
| Servo parameters | Configure servo operation | Gain settings, feedback configuration |
| Communication parameters | Configure data exchange | IP address, baud rate, timeout |
| Process parameters | Define production conditions | Pressure, temperature, process setpoint |
| Quality parameters | Define acceptance criteria | Test limits, inspection thresholds |
| Calibration parameters | Relate measurements to physical quantities | Offset, scale factor, calibration coefficients |
| Safety-related parameters | Configure supported safety functions | Validated safety limits and monitoring settings |
| Diagnostic parameters | Configure monitoring or fault detection | Alarm thresholds, diagnostic intervals |
| Recipe parameters | Define product-specific settings | Torque target, test sequence settings |
| Access parameters | Define permitted configuration or access behavior | User roles and access settings |

These categories can overlap. For example, a pressure limit may be a process parameter, a quality parameter, and part of a safety-related control strategy. Its classification should reflect its actual function and required governance.

## 4. Parameter vs. Program vs. Recipe

These terms are related but should not be treated as interchangeable.

| Item | Meaning | Example |
| --- | --- | --- |
| Program | Logic or instructions defining actions | PLC sequence or robot program |
| Parameter | Configurable value influencing system behavior | Conveyor speed limit |
| Recipe | A grouped set of settings for a product or process | Product-specific test settings |
| Calibration data | Values relating measured signals to known references | Sensor offset and scale |
| Firmware | Embedded software controlling a device | VFD firmware |
| Hardware configuration | Definition of installed hardware and its arrangement | PLC rack and I/O modules |
| Runtime data | Values generated during operation | Cycle count or live measurement |
| Retentive data | Runtime values retained across defined restart conditions | Stored production counter |

A PLC project may contain parameter-like constants, while a drive may store parameters internally. A recipe may be stored in an HMI or database and transferred to a machine when a product changes.

The backup process must account for these different storage locations.

## 5. Why Historical Parameter Backups Matter

Consider a motor that begins tripping after maintenance. The PLC program has not changed, but the VFD acceleration time has been reduced and the current limit has been altered.

A historical parameter record allows maintenance to compare the current settings with the previous approved configuration.

Parameter history helps with:

Root cause analysis.

Identifying unauthorized or undocumented changes.

Recovering from incorrect commissioning.

Restoring validated machine settings.

Investigating changes in cycle time or product quality.

Comparing behavior before and after a retrofit.

Supporting vendor troubleshooting.

Preserving calibration and process configuration history.

Demonstrating configuration control during audits.

Without historical values, an engineer may be forced to reconstruct settings from incomplete notes or rely on memory. Neither is a sensible recovery strategy.

## 6. Parameter Identification and Metadata

A parameter backup must identify both the machine and the parameter context.

Recommended fields include:

| Field | Purpose |
| --- | --- |
| Machine ID | Identifies the physical machine |
| Device ID | Identifies the specific PLC, drive, CNC, or other device |
| Parameter name | Human-readable setting name |
| Parameter number | Manufacturer-defined parameter identifier |
| Parameter group | Functional category |
| Value | Recorded parameter value |
| Unit | Engineering unit, if applicable |
| Data type | Integer, floating point, Boolean, string, enumeration, or other type |
| Valid range | Supported range from manufacturer documentation |
| Source | Controller upload, engineering project, recipe, or other origin |
| Capture timestamp | Date and time of capture |
| Software version | Tool version used to capture or edit the values |
| Firmware version | Device firmware associated with the settings |
| Hardware model | Exact device model |
| Status | Approved, working, unverified, or superseded |
| Change reference | Work order or approved change record |
| Validation result | Outcome of the applicable verification procedure |

For critical parameters, also record the parameter's description, applicable operating mode, dependencies, and whether a change requires a restart, recalibration, or functional test.

## 7. Parameter Value Types and Units

Parameter values must be recorded with their data type, unit, and interpretation.

| Type | Example | Important consideration |
| --- | --- | --- |
| Integer | 1200 | Confirm whether the value represents counts, milliseconds, or another unit |
| Floating point | 1.25 | Record precision and engineering unit |
| Boolean | TRUE | Record what enabled and disabled states mean |
| Enumeration | MODE_2 | Record the manufacturer's definition of each selection |
| String | AUTO | Preserve exact spelling and supported values |
| Bit field | 16#0004 | Record bit positions and their meanings |
| Scaled value | 750 | Determine whether it represents raw counts or an engineering value |
| Array | Multiple axis offsets | Preserve element order, size, and associated units |

A value without its unit or interpretation may be misleading.

For example, 100 could mean 100 milliseconds, 100 engineering units, 100 encoder counts, or 100% of a configured scale.

Similarly, a value of 1 might represent a Boolean state, a mode selection, a count, or an engineering value. Always retain the manufacturer's parameter definition.

## 8. Parameter Capture Methods

The correct capture method depends on the device and the location of its settings.

### 8.1 Controller or Device Upload

The settings are read from the physical device using a supported engineering or service tool.

Advantages:

Can represent the actual installed device configuration.

Helps identify deviations from the engineering master.

Supports actual-state capture during troubleshooting.

Limitations:

Some settings may not be readable or exportable.

Access restrictions may prevent a complete upload.

The capture may omit external recipes, runtime values, or protected settings.

The device may change during capture if the system is operating.

Record the capture method and any known limitations.

### 8.2 Engineering Project Export

Parameters are extracted from the project used to engineer the device.

Advantages:

Useful for maintaining the approved engineering baseline.

Can include parameter values and related configuration.

May support version control and change comparison.

Limitations:

The project may differ from the configuration currently running on the device.

Some runtime or retentive values may not be included.

The project may contain values that were never downloaded.

An engineering project export must not automatically be described as the actual device state.

### 8.3 Parameter Report or CSV Export

Some tools allow parameters to be exported into tables or reports.

This is useful for comparison, auditing, searching, and reporting. However, a CSV or PDF report may not be sufficient to restore the device because it might omit data types, parameter dependencies, or import-specific formatting.

Retain the native backup format when available and appropriate.

### 8.4 Database or Recipe Export

Parameters may be stored in an HMI, SCADA database, recipe manager, or production application.

Capture the associated data structures, schema, version information, and dependencies required to interpret and recover the values. For database-backed systems, use a supported, transactionally consistent backup method where required.

## 9. Master Parameters, Working Parameters, and Actual-State Parameters

Parameter records should distinguish approved reference values from unapproved edits and values read from the physical device.

| Record type | Meaning | Typical use |
| --- | --- | --- |
| Approved master parameters | Authorized reference settings | Controlled restoration |
| Working parameters | Values being edited or tested | Engineering and commissioning |
| Actual-state parameters | Values captured from the installed device | Troubleshooting and drift detection |
| Historical parameters | Values retained from an earlier point in time | Comparison and rollback |
| Recipe parameters | Settings associated with a product or process | Controlled product changeover |
| Calibration parameters | Values used to maintain measurement accuracy | Calibration and quality control |

A parameter set can be historical without having been approved. Approval status must be stored separately from the date.

## 10. Parameter History and Change Tracking

Each significant parameter change should be traceable.

A practical change record includes:

Machine ID and Device ID.

Parameter identifier and description.

Previous value.

New value.

Unit and data type.

Reason for the change.

Person or team responsible.

Date and time.

Work order or change request.

Required approval.

Expected effect.

Validation method.

Actual test result.

Rollback reference, if applicable.

Example:

| Field | Example record |
| --- | --- |
| Machine ID | TB-014 |
| Device ID | VFD-TB014-01 |
| Parameter | Acceleration time |
| Parameter ID | Manufacturer-defined identifier |
| Previous value | 5.0 s |
| New value | 7.0 s |
| Reason | Investigate acceleration-related trips |
| Change reference | WO-EXAMPLE |
| Approval status | Pending |
| Validation status | Not tested |

This is an illustrative record. The parameter identifier and actual values must come from the installed drive and the approved work record.

Do not record only the new value. The previous value is essential for comparison and recovery.

## 11. Before-and-After Parameter Comparison

A comparison should identify both value changes and changes in context.

Example:

| Parameter | Previous value | Current value | Difference | Review required |
| --- | --- | --- | --- | --- |
| Acceleration time | 5.0 s | 7.0 s | Increased | Yes |
| Maximum speed | 1500 rpm | 1500 rpm | No change | Normally no |
| Communication timeout | 2 s | 5 s | Increased | Yes |
| Motor rated current | Recorded value | Recorded value | Compare actual values | Yes if changed |
| Inspection threshold | Recorded value | Recorded value | Compare actual values | Yes if changed |

This table demonstrates the comparison method rather than prescribing values for a particular machine.

A parameter difference is not automatically an error. It must be evaluated against the equipment's design, operating conditions, manufacturer specifications, and approved requirements.

### 11.1 Comparison Rules

1.	Confirm both records refer to the same machine and device.

2.	Confirm that parameter identifiers have the same meaning in both versions.

3.	Compare units, data types, and scaling.

4.	Identify added, removed, renamed, or unsupported parameters.

5.	Separate intended changes from unexplained differences.

6.	Review interactions between related parameters.

7.	Record the assessment and required corrective action.

A raw numerical comparison can be misleading if the device firmware changes the interpretation or default behavior of a parameter.

## 12. Parameter Dependencies and Interactions

Parameters rarely operate independently.

Examples include:

Motor rated current and drive current limits.

Acceleration time and mechanical load.

Servo gain and mechanical stiffness.

Encoder resolution and position scaling.

CNC axis limits and machine travel.

PID gains and process response.

Vision thresholds and lighting conditions.

Test limits and measurement calibration.

Communication timeout and network behavior.

Changing one parameter may require reviewing other settings.

For example, increasing a drive's speed limit may affect stopping distance, process timing, mechanical loading, or downstream synchronization. A change should be evaluated at the system level rather than as an isolated number.

## 13. Safe Parameter Modification Procedure

Parameter changes should follow the plant's approved change-control and safety procedures.

1.	Identify the machine and device.

2.	Confirm the current operating state and relevant hazards.

3.	Capture the current parameter set where permitted.

4.	Verify that the capture is complete enough for the intended recovery.

5.	Identify the exact parameter and its manufacturer-defined meaning.

6.	Check permitted ranges, units, dependencies, and prerequisites.

7.	Record the previous value and proposed new value.

8.	Obtain required authorization.

9.	Apply the change using the approved method.

10.	Verify the displayed or stored value after the change.

11.	Perform the required functional, quality, and safety validation.

12.	Record results and update the historical backup repository.

Do not modify safety-related parameters, protection limits, or machine operating limits outside the authorized procedure. Some changes require specialist validation or a formal safety assessment.

## 14. Restoring Historical Parameters

A historical parameter file should not be applied merely because it belongs to the correct machine.

Before restoration, verify:

Machine ID and Device ID.

Exact target hardware model and revision.

Firmware compatibility.

Parameter-set format and software-tool version.

Parameter identifiers and supported ranges.

Dependencies on motor, encoder, sensor, or mechanical configuration.

Whether values are machine-specific or product-specific.

Whether calibration or commissioning is required after restoration.

Whether applying the values could change safety or process behavior.

Whether the selected version is approved for recovery.

After restoration, verify the imported values and perform the applicable commissioning checks. Record the restoration event and the resulting actual state.

## 15. Industrial Examples

### 15.1 VFD Parameters

Typical items to preserve include:

Motor nameplate values.

Control mode.

Acceleration and deceleration times.

Minimum and maximum frequency or speed limits.

Current limits.

Motor thermal protection settings.

Command and reference sources.

Communication settings.

Fault-handling behavior.

The exact parameter list depends on the drive model and application.

### 15.2 Servo Parameters

Relevant records may include:

Motor and feedback configuration.

Encoder resolution.

Control-loop gains.

Motion limits.

Homing configuration.

Electronic gearing.

Brake control.

Communication settings.

Tuning and commissioning records.

A servo parameter set must be checked against the installed motor, feedback device, mechanical system, and supported drive firmware.

### 15.3 CNC Parameters

Preserve supported machine parameters, axis configuration, tool and offset data where required, compensation tables, machine-builder settings, and relevant system information.

CNC parameter restoration requires particular care because some values are machine-builder-specific and can influence axis motion, travel limits, spindle operation, and machine protection.

Use the manufacturer's and machine builder's documented recovery procedures.

### 15.4 Vision Systems

Historical records may include:

Inspection thresholds.

Camera exposure and gain.

Lighting settings.

Calibration values.

Region-of-interest definitions.

Measurement tolerances.

Product recipes.

Image-processing settings.

A restored vision job should be validated against appropriate known-good and known-defective samples under the approved quality procedure.

### 15.5 PLC and Test-Bench Parameters

Preserve configurable timing values, process limits, sensor scaling, communication timeouts, recipe data, and test acceptance limits where applicable.

Do not assume every value displayed by a PLC or HMI is a static parameter. Some are live process values or retentive data and require different backup methods.

## 16. Parameter Integrity and Security

Parameter archives can be sensitive because they may reveal operating limits, process settings, network configuration, and device behavior.

Useful controls include:

Role-based access to edit and restore parameters.

Restricted write access to approved masters.

Separate approval and modification responsibilities where appropriate.

Integrity hashes for exported files.

Protected historical storage.

Audit logs for edits, imports, and restoration.

Offline or immutable recovery copies for critical systems.

Secure handling of passwords, credentials, and licensed secrets.

Documented retention and deletion rules.

A matching cryptographic hash can help establish that a file matches its recorded content. It does not prove that the parameters are correct, safe, approved, or suitable for the current machine.

## 17. Common Parameter Management Errors

1.	Saving only the new value and losing the previous value.

2.	Recording a number without its unit.

3.	Comparing parameter files from different devices without checking identity.

4.	Restoring settings from a similar but different machine.

5.	Ignoring firmware-dependent parameter behavior.

6.	Confusing recipe values with permanent machine settings.

7.	Treating an engineering project as proof of the actual installed values.

8.	Failing to record calibration changes.

9.	Changing parameters without an approved work or change record.

10.	Restoring parameters without checking hardware and motor configuration.

11.	Assuming a successful import proves correct operation.

12.	Deleting old parameter versions without reviewing retention requirements.

13.	Failing to verify whether protected or hidden parameters were included.

14.	Keeping a report that cannot be imported when a native recovery file is required.

## 18. Practical Industrial Example

A production test bench begins rejecting parts after a maintenance intervention.

The engineer captures the current PLC and test-system parameter sets, then compares them with the last approved versions.

The comparison identifies a changed inspection limit and a modified measurement scaling value. The engineer verifies the units, calibration status, and change records before concluding whether either difference contributed to the rejects.

The corrective action is tested using the approved quality procedure. The team then records the validated parameter set, updates the historical repository, and links the change to the maintenance record.

This approach avoids blindly restoring all old parameters, which could erase legitimate changes or reintroduce a previously corrected problem.

## 19. Parameter Backup Audit Checklist

Parameter sets are associated with the correct Machine ID and Device ID.

Parameter identifiers, values, data types, and units are preserved.

Hardware and firmware versions are recorded.

Capture method and source are documented.

Approved masters are distinguishable from working copies.

Previous and new values are recorded for significant changes.

Dependencies and related parameters are reviewed.

Calibration and recipe data are handled appropriately.

Safety-related changes follow approved procedures.

Historical files have suitable integrity and access controls.

Restoration compatibility is checked before import.

Post-restoration values are verified.

Required functional, quality, and safety checks are documented.

Retention rules preserve necessary historical records.

Parameter changes are linked to work orders or change records.

## 20. Interview Questions and Answers

Q1. What is a parameter backup?

A recorded copy of configurable values that influence the behavior or configuration of an industrial device or system.

Q2. What is the difference between a parameter and a program?

A program defines instructions or logic. A parameter supplies a configurable value that influences how the system operates.

Q3. Why are historical parameter versions important?

They allow engineers to compare settings over time, investigate failures, identify configuration drift, and recover an appropriate previous configuration.

Q4. Why must parameter units be recorded?

The same numerical value can have different meanings depending on its unit, scaling, or data type.

Q5. Is a parameter export from an engineering project always the actual device state?

No. The project may differ from the values currently stored in the physical device.

Q6. What should be checked before restoring drive parameters?

Verify the drive model, firmware, motor data, feedback configuration, parameter compatibility, and applicable safety and commissioning requirements.

Q7. What is parameter drift?

A difference between the actual parameter values and the designated approved reference values.

Q8. Why should previous and new values both be recorded?

They establish what changed, support root cause analysis, and provide traceability for corrective action or rollback.

Q9. Does a successful parameter import prove the machine is safe to operate?

No. The resulting configuration must be verified and subjected to the required functional, quality, and safety validation.

Q10. What is the most important principle in parameter management?

Preserve the values together with their machine identity, meaning, units, source, compatibility context, approval status, and validation history.

## 21. Final Principles

Treat parameters as controlled configuration data.

Preserve exact values, identifiers, units, and data types.

Separate approved masters, working versions, and actual-state captures.

Record the context required to interpret and restore the values.

Track significant changes with previous values, new values, and authorization.

Check dependencies and compatibility before restoration.

Validate the resulting machine behavior rather than trusting a successful import.

Retain historical records according to operational, quality, safety, and cybersecurity requirements.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\25_Backup_DR\02_Backup_Structure\02_Historical_Versions\05_Program_Version - Program version