# Recovery: Firmware Matching

## 1. Purpose and Scope

Firmware matching is the process of verifying that a device's firmware version is compatible with its hardware, application program, engineering software, communication partners, and intended operating configuration before installation, restoration, replacement, or commissioning.

Firmware is embedded software that controls how a physical device operates. It may manage startup, hardware interfaces, communication protocols, diagnostics, motion control, memory, and device-specific functions.

In industrial automation, firmware compatibility matters because two devices with the same product family name may use different hardware revisions, support different firmware features, or require different engineering software versions.

For example, a replacement PLC CPU may have the correct catalog number but a firmware version that is incompatible with the approved project or other devices in the automation network. Similarly, a drive may communicate with the PLC but behave differently if the firmware changes parameter definitions, supported control modes, or diagnostic behavior.

The objective is not to make every device run the newest firmware. The objective is to establish a known, supported, compatible, and approved combination of hardware, firmware, software, and configuration.

This topic covers:

Firmware fundamentals and terminology.

Hardware, firmware, and software compatibility.

Version identification and compatibility matrices.

PLC, HMI, VFD, servo, CNC, robot, vision, and network-device firmware.

Firmware upgrades, downgrades, and migrations.

Backup and recovery precautions.

Firmware-related failure diagnosis.

Change control, validation, and documentation.

Practical industrial examples and interview questions.

## 2. What Is Firmware?

Firmware is software stored in or associated with a hardware device that provides its embedded operating behavior.

Depending on the product, firmware may be stored in flash memory, other non-volatile memory, or a device-specific storage mechanism. It may be updated through an engineering tool, bootloader, maintenance interface, removable media, or a manufacturer-provided utility.

Firmware is distinct from the application program running on the device, although the exact boundary varies by platform.

Examples:

PLC CPU firmware manages controller-level functions and supported execution behavior.

VFD firmware implements drive control, monitoring, protection, and communication features.

Servo drive firmware manages motion-related control and feedback processing.

HMI firmware provides panel-level functions, runtime support, and hardware interfaces.

Robot controller firmware supports controller operation and robot-specific functions.

Industrial switch firmware provides network switching, management, and supported industrial protocols.

Vision sensor firmware supports image acquisition, inspection functions, and device communication.

Firmware updates can correct defects, add features, improve compatibility, or address security issues. They can also introduce compatibility changes or require a coordinated engineering change.

## 3. Firmware vs. Related Version Types

| Term | What it identifies | Example |
| --- | --- | --- |
| Hardware revision | Physical design or component revision | Revision C of a controller |
| Firmware version | Embedded software release | Firmware 3.2.1 |
| Application program version | User-developed control or application logic | PLC program revision 1.8 |
| Engineering software version | Tool used to configure or program the device | PLC engineering suite release 19 |
| Runtime version | Software environment that executes an application | HMI runtime release 8 |
| Operating system version | System software running on a computer | Windows IoT Enterprise release |
| Communication protocol version | Supported communication specification or implementation | A supported protocol revision |
| Parameter-set version | Identified collection of device settings | Approved drive parameter revision |
| Bootloader version | Code used to start or update the device | Device bootloader release |
| Library version | Reusable software components used by a project | Motion library release 4 |

These versions are related but not interchangeable. Recording only the firmware version does not establish the complete software environment needed to recover a machine.

## 4. Why Firmware Matching Matters

Firmware mismatch can cause several kinds of problems.

A project may not download to the controller.

An engineering tool may be unable to go online with the device.

A controller may reject a hardware configuration.

A communication feature may be unsupported.

A drive parameter may have different behavior or interpretation.

A robot application may require a specific controller software package.

An HMI project may require a newer runtime.

A device may fail to start after an unsupported downgrade.

A firmware update may reset selected settings.

A security or safety function may behave differently across versions.

Some incompatibilities are immediately visible. Others appear only under particular operating conditions, making them especially unpleasant during a production restart.

Firmware matching therefore belongs in spare-part replacement, disaster recovery, obsolescence planning, software installation, cybersecurity maintenance, and machine commissioning.

## 5. Firmware Compatibility Layers

Firmware compatibility should be assessed across the complete system rather than one device in isolation.

Physical Hardware and Revision

↓

Supported Firmware Version

↓

Engineering Software Compatibility

↓

Application Program and Libraries

↓

Communication and Device Dependencies

↓

Parameters and Device Configuration

↓

Functional and Safety Validation

A device can satisfy one compatibility layer while failing another. For example, a replacement CPU may support the installed firmware but still require a newer engineering software version to open and modify its project.

### 5.1 The Main Compatibility Questions

Before approving a firmware combination, determine:

1.	Does the firmware support the exact hardware model and revision?

2.	Does the engineering tool support that firmware?

3.	Does the application project support the target firmware?

4.	Are required libraries, technology packages, and licenses compatible?

5.	Can connected devices communicate with the selected version?

6.	Are the required parameters supported and interpreted correctly?

7.	Are there known upgrade or downgrade restrictions?

8.	Does the combination satisfy functional, safety, and cybersecurity requirements?

The answers should come from manufacturer documentation, compatibility tables, release notes, and the plant's approved configuration records.

## 6. Firmware Version Identification

Firmware identification must use the actual device information rather than an assumed version based on the product family.

### 6.1 Where to Find Firmware Information

Depending on the device, check:

Device diagnostic or status screen.

Controller display or system information menu.

Engineering software's online device information.

Manufacturer configuration utility.

Web-based device management page.

Firmware inventory or asset register.

Startup or diagnostic logs.

Manufacturer-approved identification commands.

The physical label usually identifies the hardware model and revision, not necessarily the currently installed firmware.

### 6.2 Record the Complete Identity

For each critical device, record:

| Field | Purpose |
| --- | --- |
| Machine ID | Identifies the machine |
| Device ID | Identifies the installed device |
| Manufacturer | Identifies the product supplier |
| Catalog or model number | Identifies the exact hardware model |
| Serial number | Identifies the individual physical unit |
| Hardware revision | Identifies the hardware design revision |
| Current firmware | Identifies the installed firmware |
| Approved firmware | Identifies the authorized target version |
| Engineering tool version | Identifies the tool used to configure the device |
| Project version | Identifies the application release |
| Compatibility evidence | Records the supporting documentation |
| Approval status | Identifies whether the combination is approved |

A useful register distinguishes the current version, required version, and approved version. They may not be identical during a controlled migration.

## 7. Understanding Version Numbers

Firmware version numbers are manufacturer-specific. There is no universal rule that applies to every industrial product.

A version may look like:

Major.Minor.Patch.Build

Example:

3.2.1.145

Possible meanings:

Major: Significant changes or compatibility boundaries.

Minor: Additional features or other changes within a release family.

Patch: Corrections to identified defects.

Build: Specific build or release identifier.

This example is illustrative only. Some manufacturers use numeric release identifiers, letter codes, hardware-specific firmware branches, or different versioning conventions.

Do not assume that version 3.2 is always newer or more compatible than version 3.1. A branch may be intended for a different hardware revision or product variant.

### 7.1 Version Number vs. Compatibility

A higher version number does not automatically mean better compatibility.

Compatibility depends on:

Supported hardware.

Application requirements.

Engineering tool support.

Connected device versions.

Known defects.

Upgrade and downgrade paths.

Safety and security requirements.

Vendor support status.

The correct version is the one approved for the intended configuration, not necessarily the numerically highest version.

## 8. Firmware Compatibility Matrix

A firmware compatibility matrix records the combinations permitted for a machine or automation system.

For example:

| Device | Hardware | Firmware | Engineering tool | Status |
| --- | --- | --- | --- | --- |
| PLC CPU | Model A, revision B | 3.2.1 | Tool 19 | Approved for the documented project |
| Remote I/O | Model R, revision A | 2.4 | Tool 19 | Approved for the PLC configuration |
| VFD | Model D, revision C | 5.1 | Drive tool 7 | Approved for the motor application |
| HMI | Model H, revision A | 8.3 | HMI tool 8 | Approved for the runtime project |
| Network switch | Model S, revision B | 6.0 | Management utility 4 | Approved for the network design |

These entries illustrate the structure of a matrix, not verified compatibility claims for real products.

The actual matrix should include relevant software dependencies, communication requirements, safety constraints, and supporting evidence.

### 8.1 Why a Matrix Is Better Than a Single Firmware List

A simple list might say that the PLC uses firmware 3.2.1. A compatibility matrix goes further by recording why that version is approved, which project it supports, and which connected devices have been verified with it.

This is particularly useful when:

Different machines use different controller revisions.

Replacement parts arrive with different firmware.

Multiple engineering software versions exist in the plant.

A vendor introduces a new firmware release.

Equipment is migrated to a newer platform.

Recovery must be performed by a different maintenance team.

## 9. Firmware Matching for PLCs

PLC firmware matching is important because firmware influences controller features, project compatibility, communication behavior, diagnostics, and supported hardware configurations.

### 9.1 PLC Information to Verify

Exact CPU catalog number.

Hardware revision.

Current firmware version.

Required firmware version.

Engineering software version.

Project format and required features.

Supported I/O modules.

Communication modules and protocol requirements.

Required libraries and technology packages.

Safety-related firmware and configuration requirements, where applicable.

### 9.2 Common PLC Firmware Problems

Project download rejected: The project may require a different firmware version or a compatible engineering software release.

Controller cannot be accessed online: The engineering tool, communication driver, controller firmware, or network configuration may be incompatible.

Hardware configuration mismatch: The project may include modules or features unsupported by the target controller or firmware.

Application behavior differs: Firmware changes, changed defaults, or conversion effects may influence application behavior and require review.

### 9.3 PLC Recovery Example

A failed PLC CPU is replaced with an approved spare. The spare powers up but has a different firmware version from the controller used for the last approved project.

A controlled approach is:

1.	Confirm the spare's exact model and hardware revision.

2.	Record the installed firmware.

3.	Identify the firmware required by the approved project.

4.	Check the manufacturer's supported upgrade or downgrade path.

5.	Confirm that the engineering tool supports the intended combination.

6.	Review the backup, dependencies, and recovery procedure.

7.	Obtain the required approval before changing firmware.

8.	Apply the supported firmware procedure if required.

9.	Restore the approved project and configuration.

10.	Complete the required commissioning and validation.

Do not assume that the firmware should be changed just because its version differs. First establish whether the existing combination is supported and approved.

## 10. Firmware Matching for HMI and SCADA

HMI and SCADA systems can involve several separate software layers.

For an HMI, these may include panel firmware, operating environment, runtime version, engineering software, and project version.

For a SCADA system, relevant layers may include the operating system, SCADA platform version, runtime components, communication drivers, database drivers, and application dependencies.

### 10.1 Verification Checklist

Confirm the exact panel or computer model.

Identify the current firmware or runtime.

Verify engineering software compatibility.

Check project conversion requirements.

Verify supported PLC communication drivers.

Check fonts, scripts, controls, and third-party components.

Confirm licensing and activation.

Verify security and user-access settings.

Check alarm, recipe, and data-logging behavior after recovery.

### 10.2 Example

An HMI panel is replaced after a display failure. The replacement panel supports the required project, but its runtime version is older than the version used to develop the approved application.

The engineering team must determine whether the project can run on that runtime, whether conversion or a supported update is required, and whether the required drivers and features are available.

A project that transfers successfully is not automatically a validated operator interface.

## 11. Firmware Matching for VFDs and Servo Drives

Drive firmware can influence control functions, supported motors, parameter behavior, communication options, and diagnostic handling.

### 11.1 VFD Compatibility Checks

Drive model and power rating.

Hardware revision.

Firmware version.

Engineering tool version.

Motor type and rated data.

Control mode.

Communication interface and protocol.

Parameter-set compatibility.

Required functional options.

Known firmware-specific limitations.

### 11.2 Servo Drive Compatibility Checks

In addition to the general drive checks, verify:

Motor and encoder combination.

Feedback interface.

Motion-control functions.

Electronic gearing and related configuration.

Supported tuning and commissioning methods.

Communication mapping.

Required safety functions and their compatibility.

### 11.3 Important Recovery Rule

A parameter file that was created for one firmware version should not be assumed to work identically on another version.

The device may reject some parameters, use different defaults, change supported ranges, or require a conversion procedure.

After a firmware change, compare the resulting configuration and verify critical settings using the manufacturer's supported method.

## 12. Firmware Matching for CNC Systems

CNC controls may combine controller firmware, machine-builder software, PLC or PMC logic, servo firmware, spindle-drive firmware, and other specialized components.

A mismatch between these layers can affect startup, axis control, machine functions, or application compatibility.

Check:

CNC control model and hardware revision.

Control firmware or system software.

Machine-builder software package.

PLC or PMC version.

Servo and spindle drive firmware.

Supported feedback hardware.

Machine-specific configuration.

Required options and licenses.

Parameter compatibility.

Vendor-supported recovery and migration procedures.

A machine builder may prescribe a specific combination of control software, drive firmware, and machine data. That combination should be treated as a coordinated system.

Do not independently update one layer merely because a newer release exists. Establish the compatibility of the complete machine configuration first.

## 13. Firmware Matching for Robots

Robot controllers often use coordinated software packages rather than a single firmware version.

Depending on the manufacturer and model, the relevant environment may include controller system software, robot-specific packages, application options, fieldbus components, safety software, and engineering tools.

Verify:

Controller model and hardware revision.

Controller system software.

Robot model compatibility.

Required application packages.

Motion and technology options.

External-axis support.

Communication and fieldbus compatibility.

Required licenses.

Safety configuration requirements.

Calibration and mastering implications.

A controller software change may affect supported application packages or require changes to the restoration procedure.

Before an update, establish how robot programs, calibration data, frames, and safety-related configuration will be preserved and validated.

## 14. Firmware Matching for Vision, Scanners, and Network Devices

### 14.1 Vision Systems

Check compatibility between the device firmware, camera model, inspection software, job format, communication interface, and required image-processing features.

An inspection job may use functions unavailable in an older firmware release. Conversely, an update may change supported features or behavior and require renewed inspection validation.

### 14.2 Barcode and Position Scanners

Verify:

Exact scanner model.

Firmware version.

Supported code formats or measurement features.

Communication protocol.

Configuration-tool compatibility.

Interface and connection requirements.

Parameter backup and restoration support.

### 14.3 Industrial Network Devices

For managed switches and communication modules, check:

Hardware model and revision.

Firmware support.

Protocol and feature requirements.

Configuration backup compatibility.

Redundancy behavior.

Security features.

Management software compatibility.

Recovery and downgrade procedures.

A firmware update to a network device can interrupt communications even when the PLC and field devices themselves remain unchanged. Plan the update around the impact on the connected process.

## 15. Firmware Upgrade vs. Downgrade

An upgrade installs a newer firmware release. A downgrade installs an earlier release.

Neither operation should be treated as a routine change without compatibility and recovery assessment.

| Factor | Upgrade | Downgrade |
| --- | --- | --- |
| Primary objective | Obtain required fixes, features, or support | Restore a previously required version |
| Compatibility risk | New version may alter behavior or dependencies | Older version may lack features or reject configuration |
| Configuration impact | May change defaults or require conversion | May not preserve newer configuration elements |
| Recovery concern | Update failure or unexpected behavior | Unsupported rollback or loss of compatibility |
| Validation | Required according to the change scope | Required according to the change scope |

### 15.1 Upgrade Assessment

Before an upgrade:

1.	Define the reason for the change.

2.	Identify the exact target firmware.

3.	Review manufacturer release notes.

4.	Check known defects and compatibility requirements.

5.	Confirm the supported upgrade path.

6.	Back up the current configuration and required data.

7.	Verify recovery media and rollback feasibility.

8.	Schedule the work and obtain approval.

9.	Perform the update under the approved procedure.

10.	Validate the resulting configuration and application.

### 15.2 Downgrade Assessment

Before a downgrade, verify that the manufacturer permits the operation for the exact hardware and firmware combination.

Some devices restrict downgrades because of changes to storage formats, security mechanisms, bootloaders, or configuration structures.

A downgrade may require intermediate versions, a special recovery method, or a complete configuration restoration.

Never assume that installing an older firmware file is a supported rollback strategy.

## 16. Firmware Release Notes

Release notes explain changes associated with a firmware release. They are a key source of information during compatibility assessment.

Review the applicable release notes for:

New features.

Fixed defects.

Known limitations.

Hardware compatibility.

Supported upgrade paths.

Changes in parameter behavior.

Changes in communication functions.

Security updates.

Required engineering software versions.

Restrictions on downgrade or recovery.

Pay attention to the release notes for the target version and any intermediate versions required by the upgrade path.

For example, a device may require an intermediate release before it can be updated to a newer major release. Skipping a required step may cause the update to fail or leave the device in an unsupported state.

## 17. Firmware Integrity and Authenticity

Firmware must come from an authorized and trustworthy source.

Preferred sources include manufacturer support portals, approved vendor packages, or plant-controlled repositories containing verified release files.

Check, where available:

Exact device model and supported hardware revisions.

Firmware version and release identifier.

File integrity using a manufacturer-provided checksum.

Digital signature or authenticity verification.

Package documentation.

Known security advisories.

Required update utilities and prerequisites.

A cryptographic hash can establish whether a file matches a known reference file, assuming the reference is trusted. It does not independently prove that the firmware is safe, compatible, or approved for the machine.

Do not use unofficial firmware packages on production equipment without the organization's formal assessment and authorization.

## 18. Firmware Update Risks

Firmware changes can introduce operational and recovery risks.

### 18.1 Operational Risks

Device unavailable during the update.

Communication loss.

Controller or drive restart.

Unexpected configuration reset.

Application incompatibility.

Changed diagnostics or default behavior.

Loss of device-specific data.

Inability to return to the previous firmware.

Need for recalibration or recommissioning.

### 18.2 Cybersecurity Risks

Firmware updates may address vulnerabilities, but update packages and update mechanisms can also be abused if poorly controlled.

Controls should include:

Authorized update sources.

Appropriate access permissions.

Approved maintenance windows.

Integrity verification.

Change records.

Network and device access controls.

Recovery planning.

Post-update verification.

A device should not remain on a vulnerable firmware version indefinitely merely because it works today. Equally, firmware should not be updated blindly without evaluating the impact on the operational technology system.

The correct decision balances cybersecurity risk, operational stability, vendor support, and validated compatibility.

## 19. Firmware Backup and Disaster Recovery

Firmware matching is essential during hardware replacement and disaster recovery because a replacement device may arrive with a different firmware version from the failed device.

### 19.1 What to Preserve

The recovery repository should record:

Approved firmware version.

Exact supported hardware models and revisions.

Authorized firmware package and its storage location.

Package integrity information, where available.

Required engineering tools.

Firmware update or recovery instructions.

Application compatibility requirements.

Required intermediate versions.

Known restrictions and warnings.

Last successful validation date.

Approval and change records.

Not every device allows firmware to be extracted from the installed hardware. Preserve authorized manufacturer-provided firmware packages and version records rather than assuming that an installed firmware image can always be read back.

### 19.2 Recovery Scenario

A PLC CPU fails during production. The available replacement has a different firmware version.

The recovery team should:

1.	Confirm the replacement's hardware identity.

2.	Identify the last approved firmware and project combination.

3.	Check whether the replacement can support that combination.

4.	Verify the supported update or downgrade route.

5.	Confirm the availability of the required firmware package and engineering tool.

6.	Preserve required application and configuration data.

7.	Perform the approved recovery procedure.

8.	Validate communication, I/O, application behavior, and applicable safety functions.

9.	Record the actual deployed firmware and project versions.

If compatibility cannot be established, the replacement should not be treated as ready for unrestricted production merely because it powers up.

## 20. Firmware Mismatch Diagnosis

When firmware incompatibility is suspected, use evidence rather than repeatedly changing versions.

### 20.1 Diagnostic Sequence

Reported Device or Application Fault

↓

Record Exact Hardware and Firmware Identity

↓

Capture Diagnostic Messages and Error Codes

↓

Verify Engineering Tool and Project Versions

↓

Check Manufacturer Compatibility Documentation

↓

Review Recent Firmware or Configuration Changes

↓

Determine the Supported Corrective Action

↓

Obtain Approval and Preserve Recovery Data

↓

Apply the Approved Correction

↓

Validate the Resulting System

### 20.2 Evidence to Capture

Exact error messages.

Device diagnostic codes.

Current and target firmware versions.

Hardware model and revision.

Engineering software version.

Application project version.

Recent change history.

Failed update logs, where available.

Relevant release notes.

Results of compatibility checks.

### 20.3 Avoid Uncontrolled Firmware Changes

Changing firmware without a clear diagnosis can introduce additional faults and destroy useful evidence.

Before changing the firmware, rule out other likely causes such as incorrect addressing, communication configuration, damaged cabling, incompatible project files, unsupported hardware modules, or licensing problems.

## 21. Firmware Governance and Change Control

Firmware should be managed as a controlled part of the machine configuration.

A typical process is:

1.	Identify the reason for a firmware change.

2.	Determine affected machines and devices.

3.	Assess operational, safety, quality, and cybersecurity impacts.

4.	Review compatibility documentation.

5.	Select the approved target version.

6.	Preserve backups and recovery information.

7.	Test on a representative or non-production system where practical.

8.	Approve the change.

9.	Schedule implementation.

10.	Execute the approved update.

11.	Verify device and application behavior.

12.	Record the actual deployed version.

13.	Update the firmware register and recovery repository.

14.	Monitor for unexpected behavior.

For safety-related systems, apply the required additional controls, independent review, and validation. Firmware changes that affect a safety function may require formal reassessment and revalidation before operation.

## 22. Firmware Register for Industrial Maintenance

A central register allows maintenance teams to identify the expected firmware configuration without inspecting every device manually.

| Field | Example or requirement |
| --- | --- |
| Machine ID | TB-014 |
| Device ID | PLC-TB014-CPU01 |
| Device type | PLC CPU |
| Manufacturer | Actual manufacturer |
| Model | Exact catalog number |
| Hardware revision | Actual hardware revision |
| Installed firmware | Actual version |
| Approved firmware | Authorized target version |
| Application version | Approved project revision |
| Engineering tool | Required software and version |
| Compatibility status | Verified, pending, or incompatible |
| Firmware package | Controlled repository reference |
| Evidence | Compatibility record or release notes |
| Last verification | Actual date |
| Change reference | Actual work order or change record |
| Approval status | Actual authorization status |

Use controlled status values and avoid vague entries such as OK, latest, or same as other machine. These descriptions are not enough to support recovery.

## 23. Practical Example: PLC Firmware and Project Mismatch

A machine's PLC CPU is replaced following hardware failure. The replacement has the correct catalog number, but the engineering software reports that the project's target firmware does not match the controller.

A disciplined investigation proceeds as follows:

Step 1: Identify the actual versions.

Record the replacement CPU model, hardware revision, installed firmware, project target version, and engineering software version.

Step 2: Confirm compatibility.

Consult the manufacturer's documentation to determine which firmware versions are supported by the exact CPU and engineering tool.

Step 3: Determine the supported solution.

Possible outcomes include updating the controller, selecting a supported project version, using a compatible engineering environment, or obtaining an approved replacement CPU with the required compatibility.

Step 4: Preserve the recovery baseline.

Keep the original approved project unchanged and preserve relevant device diagnostics and recovery files.

Step 5: Apply the authorized correction.

Use the manufacturer's supported procedure and the plant's change-control requirements.

Step 6: Validate the system.

Verify hardware configuration, communication, I/O, application behavior, interlocks, and required safety functions.

Step 7: Update the records.

Record the actual firmware version, restored project revision, test results, and approvals.

The important lesson is that a catalog-number match does not automatically establish firmware compatibility.

## 24. Practical Example: VFD Firmware and Parameter Compatibility

A replacement VFD is installed after a drive failure. Its hardware model is approved, but its firmware differs from the original drive.

Before loading the saved parameter file, the maintenance team must establish whether the parameter set is supported by the replacement firmware.

The team should verify the motor data, control mode, communication mapping, parameter definitions, and any manufacturer-documented conversion requirements.

If conversion is required, preserve the original parameter file and work on a separate copy. After restoration, verify critical settings and complete the prescribed commissioning and motion checks.

Do not conclude that the drive is correctly configured merely because the PLC can communicate with it.

## 25. Firmware Matching Checklist

### Before a Firmware Change

Identify the exact device model and hardware revision.

Record the currently installed firmware.

Identify the required or approved target firmware.

Verify engineering software compatibility.

Verify application and library compatibility.

Review manufacturer release notes.

Check supported upgrade and downgrade paths.

Assess operational, safety, quality, and cybersecurity impacts.

Verify the source and integrity of the firmware package.

Preserve required programs, parameters, and configuration data.

Confirm the recovery procedure and available recovery resources.

Obtain the required approval.

### During the Change

Follow the manufacturer's supported update procedure.

Maintain the required safe state.

Use the correct firmware package for the device.

Record update messages and any errors.

Avoid interrupting the process except as directed by the approved recovery procedure.

Do not introduce unrelated configuration changes.

### After the Change

Verify the installed firmware version.

Check device diagnostics and startup status.

Verify communication and hardware configuration.

Confirm application and parameter compatibility.

Perform the required functional tests.

Complete applicable safety and quality validation.

Confirm the system's actual deployed configuration.

Update the firmware register and backup repository.

Record approvals, results, and deviations.

## 26. Interview Questions and Answers

Q1. What is firmware?

Firmware is embedded software that controls device-level operation, interfaces, diagnostics, and supported functions.

Q2. Why is firmware matching important in industrial automation?

It helps ensure that hardware, application programs, engineering tools, communication partners, and device configurations operate together as a supported system.

Q3. Is the newest firmware always the best choice?

No. The correct version must be supported, compatible, approved, and suitable for the application's operational and security requirements.

Q4. What is the difference between firmware and an application program?

Firmware provides embedded device functionality, while the application program defines user-specific behavior, such as a PLC's machine sequence.

Q5. What should be checked before updating PLC firmware?

Check the exact CPU model, hardware revision, target firmware, engineering software, project compatibility, connected hardware, dependencies, recovery method, and required approvals.

Q6. Why might a firmware downgrade fail?

The manufacturer may restrict downgrades because of bootloader, storage-format, security, configuration, or hardware compatibility constraints.

Q7. What are firmware release notes used for?

They describe supported hardware, fixes, new features, known limitations, compatibility requirements, and upgrade or downgrade restrictions.

Q8. Why is firmware important during disaster recovery?

A replacement device may arrive with a different firmware version, and the approved application or configuration may require a specific supported combination.

Q9. Does a successful firmware update prove that the machine is safe?

No. The resulting system must undergo the required functional, safety, and process validation.

Q10. What is a firmware compatibility matrix?

It is a controlled record of verified and approved firmware, hardware, engineering software, application, and dependency combinations.

Q11. Why should firmware packages be stored in a controlled repository?

Controlled storage supports traceability, integrity verification, authorized recovery, and consistent maintenance practices.

Q12. How should a suspected firmware mismatch be investigated?

Record the exact device and software versions, capture diagnostics, consult manufacturer compatibility documentation, determine the supported correction, and validate the result.

## 27. Final Principles

Firmware is a critical part of the industrial device configuration.

Compatibility must be established across hardware, firmware, engineering software, application programs, and connected devices.

A newer version is not automatically a better or safer choice.

Verify manufacturer-supported upgrade and downgrade paths before changing firmware.

Preserve the existing recovery baseline and required device data.

Use trusted firmware packages and verify their integrity where supported.

Treat firmware changes as controlled engineering changes.

Validate the complete machine behavior after an update or recovery.

Maintain an accurate firmware register and compatibility matrix.

Do not release equipment until the required verification and authorization are complete.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\25_Backup_DR\03_Recovery\04_Software_Install - Software install