# Software/Hardware Revision

## 1. Purpose and Scope

Software/hardware revision control is the process of identifying, tracking, approving, storing, and verifying the versions of software and physical hardware used in an industrial system.

In industrial automation, a machine is not defined only by its make and model. Its actual behavior depends on the installed hardware, firmware, control software, parameters, communication configuration, and associated engineering documents.

Two machines with identical nameplates may behave differently because they have different PLC programs, drive parameters, firmware versions, or hardware revisions.

Revision control establishes exactly what version exists, what changed, why it changed, who authorized it, where it is installed, and how it can be recovered.

This topic covers:

PLC, HMI, SCADA, CNC, robot, and drive software revisions.

Hardware model and revision identification.

Firmware and engineering-tool compatibility.

Configuration baselines and version history.

Backup, restore, and recovery control.

Revision compatibility and migration.

Asset-level revision registers.

Industrial software deployment and verification.

Documentation, cybersecurity, auditability, and maintenance practices.

## 2. Essential Terminology

| Term | Meaning |
| --- | --- |
| Version | Identifier representing a software or hardware state |
| Revision | A particular controlled state or iteration of an item |
| Release | An approved version made available for a defined use |
| Build | A compiled or packaged software output produced from source and build settings |
| Firmware | Software embedded in a device that controls its internal operation |
| Hardware revision | A manufacturer-defined revision of a physical device or circuit design |
| Software baseline | An approved set of software files and related configuration information |
| Configuration baseline | An approved definition of a system's hardware, software, firmware, and relevant settings |
| Source code | Human-readable program instructions used to create executable software |
| Project file | An engineering-tool representation of a PLC, HMI, robot, or other automation application |
| Binary or executable | Machine-readable software that runs on a device or computer |
| Parameter set | Stored settings controlling device behavior |
| Compatibility | Ability of components or versions to operate together as required |
| Backward compatibility | Ability of a newer version to support specified older interfaces, formats, or behavior |
| Forward compatibility | Ability of an older version to handle specified features or formats introduced later |
| Migration | Controlled movement from an existing technology or version to another |
| Rollback | Restoration to a previously approved or other authorized safe state |
| End of support | Point at which a supplier no longer provides defined support or maintenance |
| Configuration drift | Unapproved or undocumented divergence from the approved configuration |
| Version control | Systematic tracking and management of changes between versions |
| Checksum | Value calculated from data to help detect unintended differences or corruption |
| Cryptographic hash | Digest used to identify data and support integrity verification |
| Digital signature | Cryptographic evidence used to authenticate the signer and verify signed content under the relevant trust model |

A version number is an identifier, not proof that the version is correct, approved, safe, or installed on a particular machine.

## 3. Why Revision Control Matters in Industrial Automation

### 3.1 Reliable troubleshooting

When a machine stops working, engineers need to establish which software and hardware configuration is actually running.

Without reliable revision information, troubleshooting may be based on an outdated project or a backup from a different machine.

### 3.2 Safe maintenance

A program that worked on one controller may be incompatible with another firmware revision or hardware configuration. Incorrect replacement or restoration can cause unexpected machine behavior.

### 3.3 Controlled engineering changes

Revision control connects an approved engineering change to the resulting software, hardware, and documentation revisions.

### 3.4 Repeatable production

Controlled configurations help maintain consistent behavior across machines, lines, and shifts.

### 3.5 Cybersecurity and lifecycle management

Version records help identify unsupported firmware, vulnerable software, obsolete components, and equipment requiring planned migration.

### 3.6 Auditability

An organization must be able to reconstruct the approved configuration and explain the history of significant modifications.

## 4. Different Types of Revisions

A single automation asset may contain several independently versioned items.

| Revision category | Example |
| --- | --- |
| Hardware model | PLC CPU catalog number |
| Hardware revision | PCB or device hardware revision |
| Firmware revision | PLC operating firmware version |
| Engineering software version | TIA Portal or Studio 5000 version |
| Application revision | PLC project or control program revision |
| HMI application revision | Screen, alarm, and navigation project revision |
| Drive firmware revision | Installed VFD firmware |
| Drive parameter revision | Approved motor and control parameter set |
| CNC software revision | CNC control software version |
| Robot application revision | Robot program and configuration version |
| Network configuration revision | Approved addressing and device configuration |
| Database or dashboard revision | Schema, query, dashboard, or application version |
| Documentation revision | Electrical drawing, I/O list, or operating procedure revision |

These revisions must not be treated as interchangeable. Updating a PLC program does not necessarily update the firmware. Replacing a CPU does not necessarily transfer the correct application. Updating a drawing does not physically modify the installed wiring.

## 5. Version Numbering Systems

Manufacturers and organizations use different numbering conventions. Always use the identifier defined by the manufacturer or internal configuration procedure.

### 5.1 Semantic versioning

Software projects sometimes use:

MAJOR.MINOR.PATCH

For example:

3.4.2

In conventional semantic versioning:

MAJOR increases for incompatible public-interface changes.

MINOR increases for backward-compatible functionality additions.

PATCH increases for backward-compatible fixes.

This convention is common in software development but is not a universal industrial automation standard. PLC projects, CNC systems, robot controllers, firmware, and proprietary engineering tools may use different schemes.

### 5.2 Manufacturer version identifiers

A manufacturer may identify firmware or hardware using:

Major and minor revisions.

Letter-based revisions.

Catalog numbers and product codes.

Firmware release identifiers.

Build numbers.

Hardware series or revision codes.

Never infer compatibility from the numerical order alone. Firmware version 5.2 is not automatically compatible with every project designed for 5.1.

### 5.3 Internal revision identifiers

An organization may assign controlled identifiers such as:

Asset: H7-TB-04

PLC project: H7_TB04_PLC

Application revision: REV-C

Release identifier: REL-2026-018

Engineering change: ECO-2026-018

These identifiers are illustrative. The important point is to link the asset, approved release, and change record.

### 5.4 Revision versus release

A revision represents a defined state of an item. A release indicates that a version has been approved for a specified use.

A project may have several development revisions before one is formally released. A released version may also be authorized only for testing, a specific machine, or a limited deployment rather than general production use.

## 6. Revision Control Lifecycle

Identify existing hardware and software

↓

Capture the approved baseline

↓

Record the proposed modification

↓

Develop the new revision

↓

Review and test the change

↓

Authorize the release

↓

Deploy to the designated asset

↓

Verify the installed configuration

↓

Update the revision register and documents

↓

Retain the previous approved state

The lifecycle should define controls for development, testing, approval, deployment, and production use. Not every revision should be available for installation merely because it exists.

## 7. Hardware Revision Control

Hardware revision control identifies the physical devices installed in the system and establishes whether they match the approved design.

### 7.1 What should be recorded?

Depending on the device, record:

Manufacturer.

Model and catalog number.

Serial number.

Hardware revision or series.

Firmware version, if applicable.

Electrical ratings.

Communication interface.

Installed location.

Associated asset and panel.

Date installed.

Supplier and warranty information where required.

Approved replacement or successor part.

Compatibility assessment.

Related engineering change and drawing revision.

### 7.2 Examples of industrial hardware

For a PLC, record the CPU model, series or hardware revision where applicable, firmware, communication modules, I/O modules, and relevant power-supply details.

For a VFD, record the exact drive model, power rating, hardware revision where available, firmware, and approved parameter set.

For a sensor, record the model, output type, supply voltage, connection, and relevant sensing or performance specifications.

For a CNC controller, record the controller model, applicable hardware and software identifiers, installed options, and relevant interface modules.

### 7.3 Why model identification alone is insufficient

A replacement device with a similar model name may have different:

Electrical ratings.

Terminal arrangements.

Communication capabilities.

Firmware support.

Timing or response behavior.

Environmental ratings.

Safety certifications or functional capabilities.

Engineering-tool compatibility.

A replacement must be evaluated against the actual application requirements, not merely its physical appearance or marketing description.

## 8. Firmware Revision Control

Firmware is embedded software that governs a device's internal functions. Examples include PLC firmware, drive firmware, network-device firmware, and robot-controller firmware.

Firmware changes can affect device operation even when the application program itself has not changed.

### 8.1 Reasons to update firmware

Correcting a confirmed defect.

Addressing a relevant security vulnerability.

Supporting new hardware or software features.

Resolving communication or interoperability problems.

Meeting an approved supplier recommendation.

Maintaining supportability.

Enabling a required migration.

### 8.2 Pre-update assessment

Before a firmware update, verify:

Exact device model and hardware revision.

Current firmware.

Target firmware and release notes.

Supported upgrade and downgrade paths.

Compatibility with the engineering software.

Compatibility with connected devices and application projects.

Required licenses or installation tools.

Backup and restoration arrangements.

Required downtime.

Tests and acceptance criteria.

Whether safety or cybersecurity review is required.

### 8.3 Firmware update precautions

Use an approved firmware package from an authorized source.

Verify the target device and file before installation.

Preserve required configuration and application backups.

Follow the manufacturer's prescribed update procedure.

Protect the device from interruption during critical update stages.

Verify the resulting firmware and device behavior.

Record the new revision and test results.

Do not assume a firmware downgrade is supported. Some devices restrict downgrades, require intermediate versions, or change their stored configuration during an update.

## 9. Software Revision Control

Software revision control tracks changes to the programs and configurations that determine how an automation system behaves.

### 9.1 PLC application

Relevant items include:

Source project.

Program organization and routines.

Function blocks and data structures.

Tag and I/O mappings.

Hardware configuration.

Communication settings.

Controller firmware compatibility.

Libraries and dependencies.

Retentive data assumptions.

Online edits and final saved project state.

Test and release evidence.

### 9.2 HMI and SCADA application

Relevant items include:

Screens and navigation.

Alarm definitions.

Tag mappings.

Scripts and calculations.

User roles and permissions.

Data logging configuration.

Communication drivers.

Runtime versions.

Server or client dependencies.

Dashboard and report definitions.

### 9.3 CNC and robot software

Relevant items include:

Application programs.

Machine or robot configuration.

Tool and work-coordinate assumptions.

Process parameters.

Controller software and firmware.

External-axis or peripheral configuration.

Safety-related settings.

Backup and restoration dependencies.

### 9.4 Drive and servo configurations

Relevant items include:

Motor identification.

Control mode.

Speed, torque, and acceleration limits.

Feedback-device configuration.

Communication settings.

Fault-response parameters.

Approved parameter files.

Firmware and commissioning-tool compatibility.

A parameter set is a controlled configuration even if it is not conventional source code. Losing it can make a replacement device behave very differently from the original.

## 10. Version Control, Change Control, and Configuration Management

These concepts are related but perform different functions.

| Discipline | Main purpose |
| --- | --- |
| Version control | Tracks versions and differences between files or project states |
| Change control | Governs whether a proposed modification may be implemented |
| Configuration management | Identifies and maintains the approved state and relationships of configuration items |
| Release management | Controls which version is approved and made available for a defined use |
| Deployment management | Controls installation of a release onto target systems |
| Backup management | Preserves data and configuration for recovery |
| Asset management | Tracks equipment identity, location, lifecycle, and ownership |

A version-control tool cannot independently authorize a safety-related change. Similarly, an approved change request does not prove that the correct file was deployed. Each discipline provides a different control.

## 11. Software Version Control Systems

Software development may use version-control systems such as Git or other repository tools. Industrial engineering environments may also use manufacturer-specific project archives, source-control integrations, document-management systems, or controlled backup repositories.

A version-control system can provide:

Revision history.

Change comparisons.

Author attribution.

Branching and controlled development.

Release tags.

Review records.

Traceability between changes and releases.

### 11.1 Industrial automation limitations

Not every PLC, HMI, CNC, or robot project is a plain-text software repository.

Engineering projects may contain binary files, generated data, hardware configurations, proprietary objects, or dependencies that ordinary text comparison cannot fully interpret.

For these projects, supplement version control with:

Manufacturer-supported project comparison.

Exported source or structured reports where appropriate.

Hardware and firmware inventories.

Approved project archives.

Documented deployment records.

Functional verification.

Hashes or other integrity checks for stored artifacts.

### 11.2 Online edits

An online edit changes the running controller without following the same offline engineering sequence as a conventional download.

Online edits require specific controls because the controller may temporarily contain changes that are not reflected in the saved project.

A controlled process should establish:

Who is authorized to perform online edits.

How the change is reviewed and recorded.

Whether testing is required before acceptance.

How the saved project is synchronized with the controller.

How the final revision is approved.

How the final backup is verified.

The running controller and the engineering laptop must not be assumed to contain identical versions merely because the connection is healthy.

## 12. Establishing a Software Baseline

A software baseline should represent the approved application and the supporting configuration needed to identify, reproduce, or recover it.

For a PLC-based machine, a baseline package may include:

Asset identifier.

PLC model and serial number where applicable.

Firmware version.

Engineering software version.

Approved native project file.

Relevant libraries and dependencies.

Hardware and network configuration.

Controller data or parameters where required.

Required passwords or recovery credentials handled through approved secure storage.

Release identifier and approval record.

Test results and acceptance evidence.

Relevant drawings and I/O lists.

Date captured and responsible engineer.

File integrity information where appropriate.

A backup file alone may be insufficient if the engineering software version, libraries, licenses, device configuration, or recovery prerequisites are missing.

## 13. Hardware and Software Compatibility Matrix

A compatibility matrix documents which combinations of hardware, firmware, engineering software, and application versions are supported or approved.

| Component | Current state | Proposed state | Required assessment |
| --- | --- | --- | --- |
| PLC CPU | Existing model and firmware | Same CPU with updated firmware | Project and firmware compatibility |
| PLC engineering software | Installed tool version | Proposed tool version | Project conversion and support |
| Remote I/O | Existing adapter and modules | Replacement adapter or modules | I/O mapping and communication |
| HMI | Existing runtime | Updated runtime | Tag, driver, and screen compatibility |
| VFD | Existing firmware and parameters | Replacement drive or firmware | Motor, control, and interface compatibility |
| Industrial network | Existing topology | Revised topology | Addressing, traffic, access, and communication |

The matrix should distinguish manufacturer-supported combinations from combinations that have been locally tested and approved. Local testing does not automatically establish supplier support.

## 14. Software Migration and Project Conversion

Opening an older project in a newer engineering environment may trigger a conversion or upgrade.

Possible consequences include:

Modified project format.

Changed library versions.

Unsupported or substituted components.

Changed default settings.

Different compilation behavior.

Altered firmware requirements.

Changes in available instructions or features.

Incompatibility with older engineering tools.

A safe migration process is:

1.	Preserve the original project unchanged.

2.	Identify the exact current engineering environment.

3.	Review conversion requirements and release notes.

4.	Create a separate working copy.

5.	Perform the conversion under controlled conditions.

6.	Review warnings and errors.

7.	Compare the converted project with the original.

8.	Compile and test using the supported tools.

9.	Validate behavior in a suitable test environment or controlled commissioning process.

10.	Approve the new baseline only after the required acceptance criteria are met.

A project that compiles successfully is not necessarily functionally correct. Compilation proves only certain forms of technical validity.

## 15. Backups, Restore, and Revision Integrity

Revision control and backup management must work together.

A useful backup strategy identifies:

What must be backed up.

How often it must be captured.

Where copies are stored.

Who can access or modify them.

How integrity is checked.

How restoration is tested.

How long each version is retained.

How recovery time requirements are met.

### 15.1 Before and after a change

Before a change, preserve the required approved configuration.

After a change, preserve the resulting configuration once the appropriate verification and release requirements have been met.

Label each package with meaningful information, such as:

Asset: H7-TB-04

System: PLC

Release: REL-2026-018

Engineering change: ECO-2026-018

Controller firmware: Recorded version

Project revision: Recorded revision

Status: Approved for production

Captured: Recorded date

The values above describe a format, not an actual controller record.

### 15.2 Integrity checks

A cryptographic hash can help establish whether a file has changed since the hash was calculated.

For example, a SHA-256 digest can be recorded alongside a backup. Recalculating the digest and comparing it with the recorded value can reveal whether the file differs.

However, a matching hash does not prove that the file is correct, safe, authorized, or suitable for the target controller. It provides evidence about file integrity, not engineering validity.

### 15.3 Restore testing

A successful backup operation does not prove that recovery will work.

Where feasible and appropriate, verify restoration in a controlled environment. For operational technology, restoration testing must account for controller compatibility, licenses, firmware, communication configuration, and the risk of accidentally overwriting a production system.

## 16. Configuration Drift

Configuration drift occurs when the installed system diverges from the approved baseline.

Common causes include:

Unrecorded PLC online edits.

Temporary parameter changes.

Replacement components with different firmware.

Direct changes to HMI or SCADA projects.

Uncontrolled file copies.

Incomplete deployment records.

Supplier service interventions.

Missing as-built updates.

### 16.1 Detecting drift

Useful controls include:

Periodic comparison with approved projects.

Hardware and firmware inventory checks.

Parameter uploads and comparisons where supported.

Review of controller diagnostics and change logs.

Asset-level configuration audits.

Controlled backups following authorized interventions.

Monitoring of unexpected device or software changes.

Not every difference is unauthorized. Retentive data, counters, timestamps, and live process values may change during normal operation. Engineers must distinguish expected runtime variation from a change in the controlled application or configuration.

## 17. Revision Register for Industrial Equipment

A revision register connects the physical asset to its actual approved configuration.

Recommended fields include:

| Field | Purpose |
| --- | --- |
| Asset ID | Unique equipment identification |
| Location | Plant, line, machine, or panel |
| System | PLC, HMI, CNC, robot, VFD, SCADA, or network |
| Manufacturer and model | Device identification |
| Serial number | Individual device identification where applicable |
| Hardware revision | Installed physical revision |
| Firmware revision | Installed device firmware |
| Engineering tool version | Tool required to work with the project |
| Application revision | Approved project revision |
| Configuration baseline ID | Link to the controlled baseline |
| Last verified date | Date of configuration verification |
| Engineering change ID | Link to the authorizing change |
| Backup location | Controlled reference to the stored package |
| Status | Approved, under review, obsolete, or other defined state |
| Responsible owner | Accountable function or role |

Avoid storing credentials or sensitive configuration secrets in a general-purpose register. Use approved access-controlled systems for such information.

## 18. Practical Example: PLC Revision Upgrade

Assume a machine uses a PLC whose application must be updated to improve fault diagnostics.

### Existing configuration

PLC hardware: Existing approved CPU.

Firmware: Recorded installed version.

Application: Approved baseline revision.

HMI: Existing released application.

Documentation: Current approved drawings and I/O list.

### Proposed change

Add a diagnostic function and associated HMI alarm.

### Required controls

1.	Identify the installed controller and project.

2.	Confirm whether a firmware change is necessary. Do not upgrade firmware merely because an application change is being made.

3.	Raise and assess the engineering change.

4.	Capture the current approved project and required controller data.

5.	Modify the application in a controlled working copy.

6.	Review logic, tag mapping, alarm behavior, and dependencies.

7.	Compile and conduct the required offline or simulated tests.

8.	Approve the release and deployment plan.

9.	Download or apply the modification under the approved procedure.

10.	Perform the required functional and regression tests.

11.	Compare the installed configuration with the approved release.

12.	Update the revision register and associated documentation.

13.	Retain the previous approved baseline according to the recovery and retention procedure.

14.	Monitor the change's effectiveness where required.

The final record should make it possible for another qualified engineer to determine exactly what changed and reproduce the approved engineering state without relying on the original engineer's memory.

## 19. Revision Control in Industry 4.0 Systems

Industry 4.0 environments introduce additional configuration items beyond PLC projects.

These may include:

OPC UA server and client configuration.

MQTT broker and topic configuration.

Node-RED flows and installed nodes.

SCADA tag databases.

SQL schemas and stored procedures.

Grafana dashboards and data-source definitions.

Edge gateways.

Industrial PC operating-system images.

Network and firewall configurations.

Data transformation logic.

API integrations and certificates.

A dashboard revision can affect reported values even if the PLC is unchanged. A SQL schema change can break historical queries. A driver update can change data types or communication behavior.

Therefore, revision control should include application dependencies and interfaces, not just controller programs.

For a Node-RED and SQL-based system, a controlled release could identify:

Flow export and revision.

Node-RED runtime and relevant package versions.

PLC connection settings without exposing secrets.

Database schema revision.

SQL objects modified.

Dashboard and query versions.

Network dependencies.

Test results for data accuracy, timestamps, and failure handling.

Recovery steps for the previous working configuration.

## 20. Cybersecurity and Access Control

Revision management is also a cybersecurity control because unauthorized software or firmware changes can affect machine availability, integrity, and safety.

Appropriate measures may include:

Role-based access.

Individual user accounts where supported.

Restricted engineering access.

Approved software and firmware sources.

Controlled removable media.

Secure storage of credentials.

Protected backups.

Review of vendor access.

Audit logs and change records.

Vulnerability and support-status monitoring.

Network segmentation and approved remote-access arrangements.

Access control must remain practical for maintenance. The objective is to ensure that only authorized personnel make controlled changes while preserving safe emergency response and recovery capability.

For safety-related systems, cybersecurity changes must be assessed for their potential effects on the safety functions and supporting architecture.

## 21. Common Mistakes

| Mistake | Why it is a problem | Correct practice |
| --- | --- | --- |
| Keeping only the latest file | Earlier approved states cannot be reconstructed | Retain controlled revisions according to policy |
| Using filenames such as FINAL_NEW | Identity and approval are ambiguous | Use controlled release identifiers |
| Recording PLC software but not firmware | Compatibility may be misunderstood | Track application, hardware, and firmware separately |
| Assuming the laptop project matches the PLC | Online edits may create differences | Compare and verify the actual installed state |
| Updating firmware without impact analysis | Compatibility or behavior may change | Review support requirements and test the upgrade |
| Treating a successful compile as acceptance | Runtime behavior remains unproven | Perform required functional and regression testing |
| Backing up without testing recovery | Backup may be incomplete or unusable | Verify integrity and test restoration where feasible |
| Ignoring drive parameters | Replacement hardware may behave incorrectly | Capture and control approved parameter sets |
| Failing to record asset-level deployment | Machines may run different revisions unknowingly | Verify each affected asset |
| Storing secrets in open revision records | Credentials may be exposed | Use secure credential storage and access controls |
| Overwriting the original project during conversion | Recovery and comparison become difficult | Preserve the original and convert a separate copy |
| Assuming a matching hash proves correctness | Integrity is confused with validity | Combine integrity checks with authorization and testing |

## 22. Practical Revision Audit Checklist

### Identification

Asset and device identities are recorded.

Hardware model and relevant revision are recorded.

Firmware and application versions are recorded separately.

Engineering software and dependencies are identified.

Approved baseline is identifiable.

### Change and release

The revision is linked to an authorized change where required.

Technical impact and compatibility have been assessed.

The release status and permitted use are clear.

Required reviews and approvals are recorded.

Deployment targets are defined.

### Backup and recovery

Required pre-change configuration is preserved.

Backup files are stored in a controlled location.

Integrity and recovery prerequisites are addressed.

Restore procedures are documented.

Previous approved revisions are retained according to policy.

### Verification and records

Installed configuration matches the approved release.

Required functional and regression tests are complete.

Firmware and parameter changes are recorded.

Related drawings and procedures are updated.

Asset-level revision registers are updated.

Deviations are documented and dispositioned.

Access and change records are retained as required.

## 23. Interview Questions and Answers

### Q1. What is software/hardware revision control?

It is the controlled identification, tracking, approval, storage, deployment, and verification of software and hardware versions used in a system.

### Q2. What is the difference between a version and a baseline?

A version identifies a particular state of an item. A baseline is an approved reference configuration that identifies the relevant versions and settings of a system.

### Q3. What is the difference between firmware and application software?

Firmware is embedded software governing a device's internal operation. Application software implements the specific machine, process, or user functionality. Their exact boundaries depend on the equipment architecture.

### Q4. Why must hardware and firmware revisions be recorded separately?

The same hardware model may support different firmware releases, and firmware differences can affect compatibility, behavior, and supportability.

### Q5. Why is a PLC backup not always sufficient for recovery?

Recovery may also require compatible engineering software, libraries, firmware, hardware configuration, controller data, licenses, network settings, and documented restoration procedures.

### Q6. What is configuration drift?

It is an undocumented or unauthorized difference between the installed configuration and its approved baseline.

### Q7. What is the difference between version control and change control?

Version control tracks changes to files or project states. Change control determines whether a modification is authorized and under what conditions it may be implemented.

### Q8. Why is firmware updating risky?

It may change device behavior, compatibility, configuration requirements, or supported features. A failed update can also interrupt operation or complicate recovery.

### Q9. How do you verify that the correct PLC program is running?

Identify the correct controller, compare the online and approved offline projects using the supported tools, verify the relevant configuration and revision identifiers, and retain the required evidence. A filename or download timestamp alone is insufficient.

### Q10. How does revision control support maintenance?

It helps engineers identify the installed configuration, restore a known approved state, avoid incompatible replacements, troubleshoot changes, and plan obsolescence migrations.

### Q11. Does a matching checksum prove that a program is correct?

No. It helps verify that data matches the data used to calculate the recorded checksum. It does not establish that the program is authorized, safe, functionally correct, or suitable for the machine.

### Q12. What should happen after an authorized software deployment?

Perform the required tests, verify the installed configuration, update the baseline and asset register, preserve recovery information, and complete the required documentation and release records.

## 24. Key Principles to Remember

Hardware, firmware, application software, engineering tools, and parameters are separate configuration items.

An identifier is not proof of authorization or correctness.

A controlled baseline represents an approved system state.

Version control does not replace engineering change authorization.

Successful compilation does not replace functional validation.

A backup is useful only when its contents and recovery prerequisites are understood.

Online edits must be reconciled with the saved and approved project.

Every affected machine must be verified individually when configurations can differ.

Industry 4.0 applications, databases, and network configurations also require revision control.

Revision history must support troubleshooting, auditability, safe recovery, and long-term equipment ownership.

The practical objective is simple: an engineer should be able to identify what is installed, determine whether it is approved, understand how it changed, and recover or modify it without guesswork.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\30_Doc_Control\02_Control_Elements\06_Master_Copies - Master copies