# Network Change Management

## 1. Purpose and Scope

Network change management is the controlled process of planning, assessing, approving, implementing, verifying, documenting, and maintaining changes to industrial communication networks and their associated configurations.

In industrial automation, a network change can affect communication between PLCs, HMIs, SCADA systems, CNC controllers, robots, VFDs, servo drives, remote I/O, industrial PCs, sensors, gateways, databases, and production monitoring systems.

A network change is not limited to replacing a cable or changing an IP address. It can include modifying VLANs, routing, firewall rules, communication protocols, switch configurations, network topology, redundancy, addressing, bandwidth, time synchronization, or access permissions.

The core principle is that a network change must preserve required communication, operational availability, cybersecurity, and machine behavior.

For maintenance and automation teams, even a small network modification can stop a production line if it affects PLC-to-remote-I/O communication, drive control, robot coordination, or SCADA data collection.

## 2. Essential Network Terminology

| Term | Meaning |
| --- | --- |
| Industrial network | Communication infrastructure connecting industrial devices and systems |
| Topology | Physical or logical arrangement of network devices and connections |
| IP address | Logical address identifying an interface within an IP network |
| Subnet mask | Defines the network and host portions of an IPv4 address |
| Default gateway | Router used to reach destinations outside the local subnet |
| MAC address | Link-layer address associated with a network interface |
| VLAN | Logical separation of network traffic at Layer 2 |
| Switch | Connects devices within an Ethernet network |
| Router | Forwards packets between IP networks |
| Firewall | Controls traffic according to configured security rules |
| Managed switch | Switch with configurable and observable network functions |
| Port | Physical interface or logical communication endpoint |
| Protocol | Rules governing communication between systems |
| Bandwidth | Available communication capacity, commonly expressed in bits per second |
| Latency | Time taken for data to travel between endpoints |
| Jitter | Variation in packet delay |
| Packet loss | Data packets that fail to reach their destination |
| Redundancy | Alternate resources or paths intended to maintain service during failures |
| Network baseline | Approved reference configuration of the network |
| Network segmentation | Separation of systems into distinct security or operational zones |
| Configuration drift | Unapproved or unintended deviation from the approved configuration |
| Firmware | Device software that controls hardware operation |
| QoS | Quality of Service mechanisms that prioritize selected traffic |
| Port mirroring | Copying selected switch traffic to a monitoring interface |
| NAT | Network Address Translation, which modifies IP addressing information in traffic |

## 3. Why Network Changes Require Formal Control

### 3.1 Production availability

Changing switch ports, addressing, VLAN membership, or routing can disconnect equipment or interrupt communication between controllers.

### 3.2 Machine operation

Industrial networks can carry commands, status, interlocks, feedback, and time-critical control data. A communication interruption may cause equipment to stop, enter a fault state, or require controlled recovery.

### 3.3 Safety

Network changes can affect safety-related communications or diagnostic visibility. A normal Ethernet connection must not automatically be assumed to provide a safety-rated communication path.

Safety-related communication must be assessed and validated according to the actual system architecture and applicable safety requirements.

### 3.4 Quality and traceability

Communication failures can result in missing measurements, incomplete test records, incorrect timestamps, lost production data, or unavailable quality results.

### 3.5 Cybersecurity

Opening firewall ports, connecting engineering laptops, changing VLANs, or enabling remote access can introduce unauthorized access paths.

### 3.6 Recoverability

Without a verified configuration backup, network diagrams, and port records, recovery from a failed change may take considerably longer than the original modification.

## 4. Common Network Change Triggers

| Trigger | Example | Required assessment |
| --- | --- | --- |
| Hardware replacement | Replacing a managed switch | Port configuration, firmware, VLANs, and compatibility |
| IP addressing | Changing a PLC IP address | Duplicate addresses, routes, device references, and client configuration |
| Network expansion | Adding remote I/O | Capacity, addressing, topology, and control-system impact |
| Machine relocation | Moving a CNC machine | Cable routes, subnet, switch port, and communication dependencies |
| Segmentation | Introducing a production VLAN | Routing, firewall rules, and required traffic flows |
| Cybersecurity remediation | Restricting unused ports | Legitimate dependencies and recovery access |
| Firmware upgrade | Updating a switch or gateway | Feature compatibility, reboot behavior, and rollback |
| Communication fault | Intermittent PLC-to-drive communication | Root cause, physical layer, load, and configuration |
| SCADA integration | Connecting an industrial PC to a data network | Data paths, security boundaries, and server dependencies |
| Redundancy improvement | Introducing a redundant network path | Protocol compatibility and loop prevention |
| Obsolescence | Migrating to a replacement controller | Protocols, addressing, timing, and device support |
| Performance issue | High latency or packet loss | Traffic load, topology, errors, and device health |
| Time synchronization | Changing an NTP or PTP source | Clock accuracy, dependencies, and timestamp behavior |

A network change should be initiated by an identified requirement or problem, not by the vague hope that changing a few settings might improve things.

## 5. Industrial Network Layers and Architecture

Industrial networks commonly separate enterprise functions from production control and field-level communication.

A simplified architecture is:

Enterprise IT

↓

Industrial DMZ

↓

Supervisory and Operations Systems

↓

Cell or Area Network

↓

PLC / CNC / Robot / Drive Controllers

↓

Remote I/O and Field Devices

This is a conceptual structure, not a universal physical wiring design. Actual architectures depend on plant requirements, control-system design, safety requirements, and cybersecurity policies.

### 5.1 Enterprise IT

May contain business applications, office computers, enterprise databases, and corporate services.

### 5.2 Industrial DMZ

A demilitarized zone can mediate approved information exchange between enterprise IT and operational technology (OT).

It may host historians, data brokers, update repositories, remote-access jump hosts, or integration services, depending on the architecture.

### 5.3 Supervisory and operations systems

May include SCADA servers, HMIs, industrial historians, manufacturing applications, and monitoring systems.

### 5.4 Cell or area network

Connects controllers and devices belonging to a machine, production cell, or process area.

### 5.5 Controller and field-device networks

Carry control and monitoring communication between PLCs, remote I/O, drives, robots, instruments, and other automation equipment.

Important: These layers should not be treated as permission to route traffic freely between them. Each permitted communication path should have a defined operational purpose and appropriate security controls.

## 6. Common Industrial Network Technologies

| Technology | Typical use | Change considerations |
| --- | --- | --- |
| Standard Industrial Ethernet | Controller and device communication | Addressing, switches, topology, and traffic |
| PROFINET | Siemens-oriented industrial Ethernet ecosystem and other compatible devices | Device names, IP settings, topology, and real-time configuration |
| EtherNet/IP | Common in Rockwell Automation and compatible industrial systems | IP configuration, I/O connections, multicast, and device compatibility |
| Modbus TCP | Industrial monitoring and control integration | Unit identifiers, TCP port configuration, register mapping, and polling |
| Modbus RTU | Serial communication over supported physical interfaces | Baud rate, parity, addressing, termination, and wiring |
| EtherCAT | Real-time distributed control and motion | Topology, device order, timing, and supported hardware |
| PROFIBUS | Fieldbus communication | Bus addressing, termination, segment length, and configuration |
| CANopen | Communication in supported motion and embedded systems | Node IDs, bitrate, and device profiles |
| OPC UA | Structured industrial data exchange | Endpoint configuration, certificates, authentication, and permissions |
| MQTT | Messaging for monitoring and IIoT applications | Broker address, topic permissions, credentials, and quality of service |
| HTTP/HTTPS | Web interfaces and application integration | TLS, authentication, ports, and access restrictions |
| SNTP/NTP | Clock synchronization | Approved time source, reachability, and timestamp requirements |
| PTP | Precision clock synchronization in supported systems | Grandmaster selection, network support, and timing configuration |

The presence of Ethernet connectors does not mean two devices use the same protocol or can exchange useful data. Physical compatibility, protocol compatibility, configuration, and application-level compatibility are separate requirements.

## 7. Network Change Management Workflow

Network change trigger

↓

Identify affected assets, links, and communication paths

↓

Capture the current network state

↓

Review topology, addressing, dependencies, and baseline

↓

Assess availability, safety, cybersecurity, and quality impact

↓

Prepare the change plan and recovery plan

↓

Obtain required authorization

↓

Schedule the work and coordinate affected teams

↓

Implement the approved change

↓

Verify connectivity and application-level communication

↓

Perform functional and operational acceptance tests

↓

Update diagrams, configurations, and records

↓

Monitor stability and close the change

The testing depth should match the change risk. Replacing a cable with an approved equivalent is different from redesigning the routing between a production control network and a SCADA server.

## 8. Network Baselines and Configuration Backups

A network baseline describes the approved state of network devices, addressing, topology, and permitted communication.

### 8.1 What to capture

Network and machine identifiers.

Physical and logical topology.

Device names and locations.

IP addresses and subnet masks.

Default gateways and routes.

MAC addresses where useful for asset identification.

Switch models, firmware, and management addresses.

Switch port assignments and link settings.

VLANs and trunk configurations.

Redundancy configuration.

Firewall and access-control rules.

Protocol-specific settings.

Time synchronization configuration.

Network dependencies and required communication paths.

Backup location and date.

Approval and revision information.

Do not collect passwords, private keys, or other secrets into an ordinary network spreadsheet. Store credentials and cryptographic material through approved secure mechanisms.

### 8.2 Backup practices

1.	Identify the correct device.

2.	Retrieve its current configuration using the supported method.

3.	Determine whether the export includes all relevant settings.

4.	Record the firmware and hardware version.

5.	Store an original copy in a controlled location.

6.	Protect the backup from unauthorized changes.

7.	Verify that the configuration can be restored.

8.	Document any settings that require manual recovery.

Some switches and industrial devices do not export every setting in a single file. A configuration backup should therefore be supplemented by relevant inventory, topology, and device-specific records.

## 9. IP Addressing and Subnet Changes

IP addressing changes can affect PLC communications, HMI connections, SCADA data collection, remote engineering, gateways, and other dependent systems.

### 9.1 IPv4 fundamentals

An IPv4 address contains 32 bits, commonly written as four decimal octets.

Example:

10.110.41.111

A subnet mask or CIDR prefix determines which addresses belong to the same IP subnet.

For example, 10.110.41.111/24 normally belongs to the subnet 10.110.41.0/24, whose conventional usable host range is 10.110.41.1 through 10.110.41.254.

The correct addressing plan must be confirmed from the actual network configuration. Do not infer the subnet mask from an IP address alone.

### 9.2 Before changing an IP address

Verify the approved address plan.

Check for duplicate addresses.

Confirm the subnet mask and gateway.

Identify all systems that reference the device.

Review PLC hardware configuration and HMI connections.

Check SCADA drivers and OPC UA or other endpoints.

Check firewall rules and routing.

Determine whether a device name or protocol-specific identifier must also change.

Plan the recovery method if the device becomes unreachable.

### 9.3 Example: PLC IP address change

Suppose a PLC is moved to a different approved subnet.

A controlled change must account for the PLC's own address, engineering workstation connectivity, HMI connections, SCADA drivers, other controller connections, and any network access rules.

Changing only the PLC address may restore local engineering access while leaving production monitoring disconnected. Verification must cover the complete set of required communication paths.

## 10. Switch, VLAN, and Port Configuration Changes

### 10.1 Managed switch parameters

Common settings include:

Management IP address.

VLAN membership.

Access and trunk port configuration.

Port speed and duplex settings where applicable.

Spanning Tree settings.

Redundancy protocols.

Multicast handling and IGMP snooping.

QoS priorities.

Port security.

SNMP monitoring.

Syslog configuration.

Time synchronization.

Firmware version.

### 10.2 VLAN changes

A VLAN separates Ethernet traffic into logical Layer 2 broadcast domains.

VLANs can help separate machine cells, supervisory systems, engineering access, and other traffic categories.

However, creating a VLAN does not automatically make it secure. Routing, firewall rules, switch configuration, and access policies determine whether systems can communicate across boundaries.

### 10.3 Access and trunk ports

An access port typically carries traffic for a designated VLAN. A trunk port can carry traffic for multiple VLANs using VLAN tagging, depending on the configuration.

Incorrectly changing an access port into a trunk, or removing a required VLAN from a trunk, can disconnect devices or create unintended connectivity.

### 10.4 Port shutdown and unused ports

Disabling unused ports can reduce exposure, but the port's actual use must first be verified. An apparently idle port may be reserved for maintenance, redundancy, or a device used only during a particular production mode.

## 11. Industrial Network Topologies and Redundancy

### 11.1 Common topologies

| Topology | Characteristics | Change risks |
| --- | --- | --- |
| Star | Devices connect to a central switch | Central switch failure may affect many devices |
| Line or daisy chain | Devices connect sequentially | A link or device failure may interrupt downstream communication |
| Ring | Devices form a loop with a supported recovery mechanism | Incorrect configuration can interrupt recovery or cause loops |
| Tree | Multiple levels of switches or branches | Uplink failure may isolate a branch |
| Mesh | Multiple interconnected paths | More complex routing, redundancy, and troubleshooting |
| Point-to-point | Direct connection between two endpoints | Link or interface failure disconnects the endpoints |

### 11.2 Redundancy concepts

Industrial networks may use supported mechanisms such as Rapid Spanning Tree Protocol (RSTP), Media Redundancy Protocol (MRP), Device Level Ring (DLR), or vendor-specific redundancy methods.

These technologies are not interchangeable. Compatibility, supported topology, recovery behavior, and device capabilities must be checked.

### 11.3 Redundancy validation

A successful ping test does not prove that network redundancy works.

Validation may need to include:

Link-failure response.

Recovery time.

Controller and device reconnection behavior.

Loss of I/O or motion communication.

Alarm generation.

Application recovery.

Impact on production and quality data.

Redundancy should be tested using an approved procedure that does not introduce uncontrolled production or safety risks.

## 12. Protocol and Communication Configuration

Network changes often affect protocol settings rather than the underlying Ethernet connection.

### 12.1 PLC-to-remote-I/O communication

Verify:

Correct device identity.

IP address or protocol-specific naming.

Controller configuration.

Connection state.

I/O data exchange.

Update interval and watchdog behavior.

Device diagnostics.

Expected fault behavior after communication loss.

### 12.2 PLC-to-drive communication

Verify:

Correct drive identity and address.

Control and status word mapping.

Command and feedback data.

Communication timeout.

Fault handling.

Safe behavior during loss of communication.

Recovery after the connection returns.

### 12.3 SCADA and OPC UA

Verify:

Endpoint address.

Server and client configuration.

Certificates and trust settings.

Authentication and authorization.

Required tags and data types.

Update rates.

Quality flags and stale-data handling.

Alarm, trend, and historical-data continuity.

### 12.4 Modbus TCP

Verify:

Correct destination address.

Correct TCP port as configured by the device.

Unit identifier where applicable.

Register addresses and data types.

Byte and word order.

Polling frequency.

Device response and timeout handling.

A reachable TCP port does not prove that register mapping, scaling, or application data is correct.

## 13. Network Performance and Diagnostics

### 13.1 Important metrics

| Metric | What it tells you | Possible significance |
| --- | --- | --- |
| Link status | Whether the physical or logical link is established | Cable, port, or device problem |
| Packet loss | Whether packets fail to arrive | Faulty link, congestion, or device issues |
| Latency | Communication delay | Application responsiveness |
| Jitter | Variation in delay | Timing consistency |
| Interface errors | Physical or link-layer errors | Cable, connector, interference, or interface issue |
| Bandwidth utilization | How much link capacity is being used | Congestion or capacity concerns |
| Connection count | Active connections or sessions | Resource limits or unexpected clients |
| CPU and memory | Device resource use | Overload or software issue |
| Broadcast and multicast traffic | Distribution of group traffic | Configuration problems or excessive traffic |
| Protocol diagnostics | Application-level communication state | Device or protocol-specific fault |

### 13.2 Useful diagnostic tools

ping for basic IP reachability.

tracert or traceroute for routing-path investigation where applicable.

ipconfig on Windows to inspect local interface configuration.

arp -a to inspect the local ARP cache.

route print on Windows to inspect routing entries.

Managed-switch diagnostic counters and event logs.

Device diagnostic pages and controller fault logs.

Packet capture tools such as Wireshark, used under the site's approved cybersecurity and operational procedures.

These tools answer different questions. A successful ping does not prove that PLC I/O communication, industrial real-time traffic, OPC UA security, or application data mapping is functioning correctly.

## 14. Network Troubleshooting Sequence

A layered troubleshooting approach reduces random changes and preserves useful evidence.

Confirm the symptom and time of occurrence

↓

Identify affected devices and communication paths

↓

Check power, link LEDs, cables, and physical connections

↓

Check interface errors and switch port status

↓

Verify IP address, subnet, gateway, and duplicate addresses

↓

Check VLAN membership and routing

↓

Check firewall rules and required ports

↓

Check protocol and application configuration

↓

Review device diagnostics and packet captures if needed

↓

Implement a verified corrective action

↓

Test normal operation and fault recovery

↓

Document the root cause and corrective action

### 14.1 Example: PLC appears connected, but data is missing

Possible causes include:

The wrong PLC IP address is configured in the client.

The network connection is established but the protocol session has failed.

A firewall blocks the required traffic.

A PLC tag or data mapping has changed.

The device has a stale or invalid data value.

The application is reading the wrong register or data type.

A communication timeout has occurred.

A driver or software version is incompatible.

Diagnose the actual data path rather than assuming that a network status indicator means every layer is working.

## 15. Cybersecurity and Network Segmentation

Industrial network changes must preserve authorized communication while limiting unnecessary access.

### 15.1 Core controls

Separate IT and OT environments according to the approved architecture.

Restrict communication to required destinations and services.

Control engineering access.

Use approved remote-access methods.

Disable unnecessary services where supported and approved.

Maintain firmware and configuration inventories.

Protect credentials and cryptographic keys.

Monitor relevant network events.

Maintain tested recovery procedures.

Review changes to firewall and routing rules.

### 15.2 Firewall rule changes

A firewall change request should identify:

Source system or security zone.

Destination system or security zone.

Protocol and port.

Direction of communication.

Business or operational purpose.

Required duration, if temporary.

Owner and approver.

Testing and rollback procedure.

Avoid broad rules such as allowing unrestricted communication between entire production and enterprise networks when a narrower rule can satisfy the requirement.

### 15.3 Remote engineering access

Remote access can be essential for support, but it introduces additional risks.

Use the site's approved access process, appropriate authentication, restricted permissions, controlled sessions, and monitoring. Confirm the impact of remote sessions on active control systems before performing any engineering operation.

## 16. Network Changes Affecting Safety and Availability

Not all network communication has the same operational criticality.

A network may carry:

Non-critical monitoring data.

Production reporting data.

Machine sequence commands.

Time-sensitive control data.

Safety-related communication.

Before a change, determine which category is affected and what the machine is designed to do if communication is interrupted.

For safety-related communication, the assessment must include the applicable safety architecture, certified components where required, configuration integrity, and validation requirements.

Do not assume that ordinary Ethernet diagnostics establish the integrity of a safety function. Equally, do not assume that every industrial network fault is itself a safety-function failure. Follow the actual design and risk assessment.

## 17. Network Migration and Device Replacement

Network changes often accompany replacement of obsolete hardware.

### 17.1 Before replacement

Record:

Existing device model and firmware.

Configuration and addressing.

Port assignments and cable labels.

VLAN and redundancy settings.

Protocol dependencies.

Connected devices.

Required configuration exports.

Expected outage and recovery plan.

### 17.2 During replacement

Verify the replacement device and supported features.

Apply the approved configuration.

Confirm physical port mapping.

Verify firmware compatibility.

Confirm addressing and network membership.

Check redundancy and management access.

Validate dependent communication paths.

### 17.3 After replacement

Verify all required device connections.

Test PLC, HMI, drive, robot, CNC, and SCADA communication as applicable.

Check alarms and diagnostic counters.

Verify monitoring and time synchronization.

Update asset records and network diagrams.

Store the final approved configuration.

Monitor stability after returning to service.

A replacement switch with the same number of ports is not necessarily functionally equivalent to the old one. Features, timing, multicast behavior, redundancy support, and firmware can differ.

## 18. Network Change Testing and Acceptance

Testing must establish that the modified network meets its defined requirements.

### 18.1 Test categories

Physical connectivity.

IP addressing and routing.

VLAN and access control.

Protocol-level communication.

Application data exchange.

Performance and timing.

Redundancy and recovery.

Cybersecurity controls.

Monitoring and diagnostics.

Production and quality functions.

### 18.2 Acceptance criteria

Examples:

All required endpoints are reachable using the approved paths.

PLC-to-remote-I/O communication is healthy.

Drive commands and feedback are correct.

SCADA values update correctly and retain valid quality status.

No unexpected packet loss or interface errors occur under the defined test conditions.

Required access restrictions remain effective.

Redundancy behaves as specified.

Alarms and recovery behavior meet requirements.

Production records and timestamps remain correct.

Acceptance criteria should be defined before the change, not invented after a failed test to make the result look successful.

## 19. Rollback and Recovery Planning

A rollback plan defines how to restore the previously approved network state if the change fails.

### 19.1 Rollback preparation

Preserve the original configuration.

Confirm access to the affected device.

Record original port assignments and cable mapping.

Preserve original addressing and routing information.

Confirm recovery access if the management address changes.

Identify dependencies on upstream switches and gateways.

Establish a decision point for aborting the change.

Define the maximum permitted outage where applicable.

### 19.2 Recovery sequence

1.	Stop the change when a defined failure condition occurs.

2.	Place affected equipment in the required safe condition.

3.	Identify whether the fault is physical, configuration-related, or application-related.

4.	Restore the previous approved configuration or connection arrangement.

5.	Verify device reachability and protocol communication.

6.	Confirm the required machine and process behavior.

7.	Inform affected teams.

8.	Record the failure and recovery actions.

9.	Perform root-cause analysis before rescheduling the change.

Some network changes can lock out remote access or disrupt the very connection needed to reverse the modification. Recovery access must therefore be planned before the change begins.

## 20. Network Documentation and Change Records

Every significant network change should have enough evidence for another qualified person to understand what changed and how to recover it.

### 20.1 Change record fields

| Field | Purpose |
| --- | --- |
| Change ID | Unique reference for the modification |
| Trigger | Reason for the change |
| Affected assets | Devices, machines, and systems involved |
| Current configuration | Original network state |
| Proposed configuration | Intended network state |
| Impact assessment | Availability, safety, quality, and security effects |
| Approval | Required authorization |
| Planned window | Scheduled implementation period |
| Backup reference | Location of the original configuration |
| Test plan | Required verification activities |
| Test results | Evidence of acceptance |
| Rollback result | Recovery outcome if rollback was required |
| Updated documentation | Diagrams, port maps, and inventories |
| Responsible person | Person performing the work |
| Reviewer | Person reviewing evidence |
| Closure status | Final disposition of the change |

### 20.2 Network documentation to update

Physical network diagram.

Logical network diagram.

IP address inventory.

VLAN and subnet register.

Switch port map.

Firewall rule register.

Industrial protocol dependency list.

Device and firmware inventory.

Configuration backup index.

Troubleshooting and recovery instructions.

Documentation should represent the actual deployed state, not merely the design that was originally intended.

## 21. Practical Industrial Example: Adding an Industrial PC to a PLC Network

Problem: An industrial PC must collect PLC data and forward approved information to a monitoring application.

### Step 1: Define the requirement

Identify the data required, update rate, destination, retention requirements, and whether the PC needs read-only access or control capability.

### Step 2: Identify the correct network location

Determine whether the PC belongs on the machine cell network, a supervisory network, or another approved segment. Do not connect it directly to a production network simply because an available switch port exists.

### Step 3: Assess communication dependencies

Record the PLC address, protocol, required ports, expected data volume, and destination application.

### Step 4: Assess cybersecurity

Define required source and destination paths, account permissions, credentials, and firewall controls.

### Step 5: Prepare the change

Back up relevant configurations, define the addressing plan, obtain approval, and establish rollback steps.

### Step 6: Implement

Connect the approved interface, apply the authorized network configuration, and configure the required application endpoints.

### Step 7: Verify

Confirm:

Correct network membership.

Correct addressing.

Required PLC data access.

Correct data types and scaling.

Expected update rate.

Correct handling of stale or failed data.

Continued PLC and machine operation.

Appropriate restrictions on unauthorized access.

### Step 8: Document

Update the network diagram, address register, asset inventory, and change record.

## 22. Practical Industrial Example: Node-RED, SQL Server, and Grafana

Consider a local industrial monitoring system in which Node-RED collects PLC data, SQL Server stores measurements, and Grafana displays historical trends.

The conceptual data path is:

PLC

↓

Industrial Ethernet

↓

Node-RED data collection

↓

SQL Server

↓

Grafana visualization

The actual architecture may use separate interfaces or network segments for the PLC, application host, database, and visualization client.

### 22.1 Potential network change

Moving the industrial PC to a different switch port or subnet may affect:

PLC reachability.

Firewall rules.

Node-RED PLC connection configuration.

SQL Server connectivity.

Grafana data-source configuration.

DNS or hostname resolution.

Time synchronization.

Monitoring and remote engineering access.

### 22.2 Verification sequence

1.	Confirm the industrial PC's approved IP configuration.

2.	Verify PLC reachability.

3.	Verify the PLC protocol session and actual data updates.

4.	Confirm Node-RED processes current values rather than stale data.

5.	Verify SQL Server connection and new record insertion.

6.	Confirm Grafana can query the intended database.

7.	Compare timestamps and sample values across the pipeline.

8.	Confirm that production control remains unaffected.

9.	Update the network diagram and recovery records.

A green connection indicator in one application is not proof that the entire data pipeline is healthy. Verify each boundary separately.

## 23. Common Network Change Mistakes

| Mistake | Consequence | Prevention |
| --- | --- | --- |
| Changing an IP address without checking dependencies | HMI or SCADA disconnection | Map all dependent systems first |
| Connecting a new device to an arbitrary port | Wrong VLAN or unintended access | Follow the approved port map |
| Assuming ping proves application health | Protocol or data failures remain | Test the actual application path |
| Applying a switch backup to an incompatible model | Configuration failure or unsupported features | Verify model and firmware compatibility |
| Changing firewall rules too broadly | Unnecessary network exposure | Restrict rules to required flows |
| Changing VLANs without checking trunks | Devices become unreachable | Verify end-to-end VLAN membership |
| Ignoring multicast behavior | Unnecessary traffic or communication problems | Check protocol and switch requirements |
| Changing redundancy settings without testing | Failover does not work as expected | Validate the actual recovery mechanism |
| Replacing hardware without updating records | Future troubleshooting becomes unreliable | Update inventory and diagrams |
| Testing only during idle conditions | Production-load problems remain hidden | Test under approved representative conditions |
| Ignoring time synchronization | Incorrect timestamps or event ordering | Verify time sources and dependent systems |
| Failing to prepare recovery access | Change cannot be reversed remotely | Plan local or out-of-band recovery where appropriate |

## 24. Network Change Management Checklist

### Before the change

Change trigger and technical requirement documented.

Correct assets and communication paths identified.

Current topology and configuration captured.

IP addresses, VLANs, ports, and routes verified.

Dependencies across PLC, HMI, SCADA, drives, robots, and databases assessed.

Availability, safety, quality, and cybersecurity impacts reviewed.

Approved change plan and acceptance criteria prepared.

Required approvals obtained.

Configuration backups verified.

Rollback and recovery access confirmed.

Affected teams informed and implementation window agreed.

### During the change

Correct equipment and ports confirmed.

Approved configuration applied.

Physical connections and link states verified.

Addressing and VLAN membership checked.

Required routes and access rules verified.

Protocol-specific configuration checked.

Unexpected behavior investigated before proceeding.

### After the change

Required endpoints and applications tested.

PLC and field-device communication verified.

SCADA and data collection verified where applicable.

Performance and diagnostic counters checked.

Redundancy and recovery tested where required.

Cybersecurity controls verified.

Production and quality functions confirmed.

Network diagrams and device inventories updated.

Final configuration backed up.

Change record completed and approved for closure.

Post-change stability monitored.

## 25. Interview Questions and Answers

### Q1. What is network change management?

It is the controlled process of planning, approving, implementing, testing, documenting, and maintaining changes to network infrastructure and configuration.

### Q2. Why is industrial network change management important?

Industrial networks support control, monitoring, coordination, quality records, and operational availability. Uncontrolled changes can interrupt production or compromise security.

### Q3. What is the difference between a switch and a router?

A switch primarily forwards frames within a Layer 2 network, while a router forwards packets between IP networks. Modern devices may combine both functions.

### Q4. What is a VLAN?

A VLAN creates a logical Layer 2 broadcast domain. It can support network separation, but appropriate routing and security controls are still required.

### Q5. Why does a successful ping not prove that an industrial application works?

Ping tests basic IP reachability using ICMP. It does not prove that the required application protocol, authentication, data mapping, or control communication is functioning.

### Q6. What is the purpose of a network baseline?

It records the approved network configuration and provides a reference for troubleshooting, controlled changes, audits, and recovery.

### Q7. What should be checked before changing a PLC IP address?

The address plan, subnet, gateway, duplicate addresses, dependent HMI and SCADA connections, controller configuration, firewall rules, and recovery method.

### Q8. What is network redundancy?

Redundancy provides alternate resources or communication paths intended to maintain service when a defined failure occurs. Its effectiveness must be verified through testing.

### Q9. What is the difference between latency and jitter?

Latency is communication delay. Jitter is variation in that delay. Both can matter in time-sensitive industrial communication.

### Q10. Why is network segmentation used in OT?

It limits unnecessary communication between systems, reduces exposure, and supports controlled access between production areas and other networks.

### Q11. What should be included in a network rollback plan?

The original configuration, device and port mappings, recovery access, restoration procedure, verification steps, and conditions that trigger rollback.

### Q12. Why should network changes be tested at the application level?

Physical connectivity and IP reachability do not establish that PLC data, drive commands, SCADA values, or production records are correct.

### Q13. What is configuration drift?

It is an unintended or unauthorized deviation between the deployed network configuration and its approved baseline.

### Q14. What should maintenance do after replacing a managed switch?

Verify hardware and firmware compatibility, restore the approved configuration, check physical and logical connectivity, test dependent industrial communication, confirm security and redundancy, and update documentation.

### Q15. When is a network change complete?

When the approved change is implemented, required communication and operational tests pass, recovery arrangements remain valid, documentation is updated, and the change meets its closure criteria.

## 26. Key Principles to Remember

Identify the full communication path before changing any network component.

Capture the existing configuration and verify recovery access.

Treat IT and OT connectivity as an architectural and security decision.

Validate physical connectivity, IP networking, protocol behavior, and application data separately.

Verify VLANs, routing, firewall rules, addressing, and device dependencies.

Test redundancy and fault recovery when they are part of the design.

Use controlled access and least-privilege communication.

Check production behavior and data quality, not merely connection indicators.

Update the deployed network documentation after every significant change.

Preserve a verified baseline so the next maintenance engineer does not have to reconstruct the network from switch LEDs and optimism.

The practical maintenance principle: A network change is successful only when the required systems communicate correctly, the machine behaves as intended, security controls remain effective, and the final configuration is documented and recoverable.

# NEXT TOPIC

02_PLAN_WISE_2026\02_INDUSTRY3_0\31_Change_Mgmt\01_Triggers\05_Sensor - Sensor